{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":36,"n_cols":7,"rows_kept":36,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EBVH-D9W / ERLA11-16DW1"]
[]
[]
[]
[]
["","","","","","EBVH16S18DJ9W / ERLA16DAW1","EBVH16S23DJ9W / ERLA16DAW1"]
["Domestic hot water heating","General","","Declared load profile","","L"]
["","Average climate","","Water heating energy efficiency class","","A+"]
["COP","","","","","4.53 (1), 3.51 (2)","4.53, 3.51"]
["Space heating","Average climate water outlet 35°C","General","ηs (Seasonal space heating efficiency)","%","181"]
["","","","Seasonal space heating eff. class","","A+++"]
["","","","SCOP","","4.61"]
["","Average climate water outlet 55°C","General","Seasonal space heating eff. class","","A++"]
["","","","ηs (Seasonal space heating efficiency)","%","130"]
["","","","SCOP","","3.32"]
["Heat up time from 10°C to 50°C","hr","","","","1h15min at 7°C ambient temperature","1h07min at 7°C ambient temperature"]
["Heating capacity","Nom.","","","kW","16.0 (1), 16.0 (2)"]
["Power input","Heating","","Nom.","kW","3.53 (1), 4.56 (2)"]
["","Domestic hot water from 10°C to 50°C","","Nom.","kWh","2.44"]
["Notes","","","","","(1) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(3) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(3) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(4) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )"]
["","","","","","(5) - According to EN14825","(5) - Measured with a pressure drop of 10 kPa in the heating system at an operating condition of leaving water 47-55°C in a room with an ambient of 20°C. DB/WB 7°C/6°."]
["","","","","","(6) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(7) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )"]
["","","","","","(8) - Measured with a pressure drop of 10 kPa in the heating system at an operating condition of leaving water 47-55°C in a room with an ambient of 20°C. DB/WB 7°C/6°."]
["Heating capacity","Nom.","","","kW","","16.0, 16.0"]
["Power input","Heating","","Nom.","kW","","3.53, 4.56"]
["","Domestic hot water from 10°C to 50°C","","Nom.","kWh","","3.41"]
["Domestic hot water heating","General","","Declared load profile","","","XL"]
["","Average climate","","Water heating energy efficiency class","","","A"]
["Space heating","Average climate water outlet 55°C","General","SCOP","","","3.32"]
["","","","Seasonal space heating eff. class","","","A++"]
["","Average climate water outlet 35°C","General","SCOP","","","4.61"]
["","","","Seasonal space heating eff. class","","","A+++"]