{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":8,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EDLQ011-016C3V3"]
[]
[]
[]
[]
["","","","","","EDLQ011CA3V3","EDLQ014CA3V3","EDLQ016CA3V3"]
["Heating capacity","Nom.","","","kW","11.2 (1), 11.0 (2)","14.5 (1), 13.6 (2)","15.2 (2), 16.0 (1)"]
["Cooling capacity","Nom.","","","kW","12.4 (1), 11.6 (2)","12.8 (1), 12.6 (2)","13.6 (2), 13.9 (1)"]
["Heater capacity","Step 1","","","kW","3","3","3"]
["Power input","Cooling","","Nom.","kW","3.18 (1), 5.09 (2)","3.16 (1), 5.14 (2)","3.56 (1), 5.96 (2)"]
["","Heating","","Nom.","kW","2.43 (1), 3.10 (2)","3.37 (1), 4.10 (2)","3.76 (1), 4.66 (2)"]
["COP","","","","","4.61 (1), 3.55 (2)","4.30 (1), 3.32 (2)","3.26 (2), 4.26 (1)"]
["Dimensions","Unit","","Height","mm","1,348","1,348","1,348"]
["","","","Width","mm","1,160","1,160","1,160"]
["","","","Depth","mm","380","380","380"]
["Weight","Unit","","","kg","157","157","157"]
["Fan","Air flow rate","Heating","High","m³/min","90.0","90.0","90.0"]
["Operation range","Heating","Water side","Min.","°C","25 (5)","25 (5)","25 (5)"]
["","","","Max.","°C","55 (5)","55 (5)","55 (5)"]
["","Domestic hot water","Ambient","Min.","°CDB","-25 (5)","-25 (5)","-25 (5)"]
["","","","Max.","°CDB","35 (5)","35 (5)","35 (5)"]
["","","Water side","Min.","°C","25","25","25"]
["","","","Max.","°C","80 (5)","80 (5)","80 (5)"]
["Sound power level","Heating","","Nom.","dBA","64 (6)","64 (6)","66 (6)"]
["","Cooling","","Nom.","dBA","64 (7)","66 (7)","69 (7)"]
["Sound pressure level","Heating","","Nom.","dBA","51 (8)","51 (8)","52 (8)"]
["","Cooling","","Nom.","dBA","50 (8)","52 (8)","54 (8)"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A"]
["","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","3.40","3.40","3.40"]
["Space heating","Average climate water outlet 55°C","General","SCOP","","3.09","3.16","3.06"]
["","","","Seasonal space heating eff. class","","A+","A+","A+"]
["","Average climate water outlet 35°C","General","SCOP","","3.98","3.90","3.80"]
["","","","Seasonal space heating eff. class","","A++","A++","A+"]
["Power supply","Name","","","","V3","V3","V3"]
["","Phase","","","","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","230","230","230"]
["Notes","","","","","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )"]
["","","","","","(3) - Condition 3: heating Ta DB -7°C (RH85%) - LWC 35°C","(3) - Condition 3: heating Ta DB -7°C (RH85%) - LWC 35°C","(3) - Condition 3: heating Ta DB -7°C (RH85%) - LWC 35°C"]
["","","","","","(4) - Condition 4: heating Ta DB -7°C (RH85%) - LWC 45°C","(4) - Condition 4: heating Ta DB -7°C (RH85%) - LWC 45°C","(4) - Condition 4: heating Ta DB -7°C (RH85%) - LWC 45°C"]
["","","","","","(5) - Including BUH and / or booster heater. For more details see data-book","(5) - Including BUH and / or booster heater. For more details see data-book","(5) - Including BUH and / or booster heater. For more details see data-book"]
["","","","","","(6) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(6) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(6) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(7) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(7) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(7) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","(8) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(8) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(8) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information."]
["","","","","","(9) - Including piping + PHE; excluding expansion vessel","(9) - Including piping + PHE; excluding expansion vessel","(9) - Including piping + PHE; excluding expansion vessel"]