{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":29,"n_cols":11,"rows_kept":29,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ETBX12E9W / EPRA08-12EV"]
[]
[]
[]
[]
["","","","","","ETBX12EJ9W / EPRA08EAV3","ETBX12EF9W / EPRA08EAV3","ETBX12EJ9W / EPRA10EAV3","ETBX12EF9W / EPRA10EAV3","ETBX12EJ9W / EPRA12EAV3","ETBX12EF9W / EPRA12EAV3"]
["Indoor unit","","","","","","ETBX12EF9W","","ETBX12EF9W","","ETBX12EF9W"]
["Heating capacity","Min.","","","kW","3.44 (1)","3.44 (1)","3.44 (1)","3.44 (1)","3.44 (1)","3.44 (1)"]
["","Nom.","","","kW","6.17 (2)","6.17 (2)","6.17 (2)","6.17 (2)","6.17 (2)","6.17 (2)"]
["","Max.","","","kW","7.95 (1)","7.95 (1)","9.25 (1)","9.25 (1)","9.97 (1)","9.97 (1)"]
["Cooling capacity","Nom.","","","kW","6.81 (3), 6.47 (4)","6.81 (3), 6.47 (4)","7.97 (3), 6.47 (4)","7.97 (3), 6.47 (4)","8.62 (3), 6.47 (4)","8.62 (3), 6.47 (4)"]
["Power input","Heating","","Min.","kW","0.72 (5)","0.72 (5)","0.72 (5)","0.72 (5)","0.72 (5)","0.72 (5)"]
["","","","Nom.","kW","1.25 (2)","1.25 (2)","1.25 (2)","1.25 (2)","1.25 (2)","1.25 (2)"]
["","","","Max.","kW","1.69 (5)","1.69 (5)","2.04 (5)","2.04 (5)","2.28 (5)","2.28 (5)"]
["","Cooling","","Nom.","kW","2.15 (3), 1.16 (4)","2.15 (3), 1.16 (4)","2.66 (3), 1.16 (4)","2.66 (3), 1.16 (4)","2.96 (3), 1.16 (4)","2.96 (3), 1.16 (4)"]
["COP","","","","","4.92 (2)","4.92 (2)","4.92 (2)","4.92 (2)","4.92 (2)","4.92 (2)"]
["EER","","","","","3.17 (3), 5.56 (4)","3.17 (3), 5.56 (4)","3.00 (3), 5.56 (4)","3.00 (3), 5.56 (4)","2.91 (3), 5.56 (4)","2.91 (3), 5.56 (4)"]
["Space heating","Average climate water outlet 55°C","General","SCOP","","3.47","3.47","3.48","3.48","3.48","3.48"]
["","","","Seasonal space heating eff. class","","A++","A++","A++","A++","A++","A++"]
["","Average climate water outlet 35°C","General","SCOP","","4.79","4.79","4.82","4.82","4.82","4.82"]
["","","","Seasonal space heating eff. class","","A+++","A+++","A+++","A+++","A+++","A+++"]
["Energy Efficiency Range","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Notes","","","","","(1) - Capacity according to standard EN14511 and valid for heated water range dT = 3~8°C at Ta 7°C","(1) - Capacity according to standard EN14511 and valid for heated water range dT = 3~8°C at Ta 7°C","(1) - Capacity according to standard EN14511 and valid for heated water range dT = 3~8°C at Ta 7°C","(1) - Capacity according to standard EN14511 and valid for heated water range dT = 3~8°C at Ta 7°C","(1) - Capacity according to standard EN14511 and valid for heated water range dT = 3~8°C at Ta 7°C","(1) - Capacity according to standard EN14511 and valid for heated water range dT = 3~8°C at Ta 7°C"]
["","","","","","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(3) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(3) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(3) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(3) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(3) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(3) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB"]
["","","","","","(4) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(4) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(4) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(4) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(4) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(4) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB"]
["","","","","","(5) - Power input is total input of indoor and outdoor units, including the circulation pump; according to EN14511","(5) - Power input is total input of indoor and outdoor units, including the circulation pump; according to EN14511","(5) - Power input is total input of indoor and outdoor units, including the circulation pump; according to EN14511","(5) - Power input is total input of indoor and outdoor units, including the circulation pump; according to EN14511","(5) - Power input is total input of indoor and outdoor units, including the circulation pump; according to EN14511","(5) - Power input is total input of indoor and outdoor units, including the circulation pump; according to EN14511"]
["","","","","","(6) - Test at Ta DB/WB 7°C/6°C. According to EN 16147.","(6) - Test at Ta DB/WB 7°C/6°C. According to EN 16147.","(6) - Test at Ta DB/WB 7°C/6°C. According to EN 16147.","(6) - Test at Ta DB/WB 7°C/6°C. According to EN 16147.","(6) - Test at Ta DB/WB 7°C/6°C. According to EN 16147.","(6) - Test at Ta DB/WB 7°C/6°C. According to EN 16147."]
["","","","","","(7) - DB/WB 7°C/6°C - LWC 35°C (dT=5°C) with pump at full speed","(7) - DB/WB 7°C/6°C - LWC 35°C (dT=5°C) with pump at full speed","(7) - DB/WB 7°C/6°C - LWC 35°C (dT=5°C) with pump at full speed","(7) - DB/WB 7°C/6°C - LWC 35°C (dT=5°C) with pump at full speed","(7) - DB/WB 7°C/6°C - LWC 35°C (dT=5°C) with pump at full speed","(7) - DB/WB 7°C/6°C - LWC 35°C (dT=5°C) with pump at full speed"]