{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":11,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DV3P"]
[]
[]
[]
[]
["","","","","","EWAA004D2V3P","EWAA006D2V3P","EWAA008D2V3P","EWAA011DAV3P","EWAA014DAV3P","EWAA016DAV3P"]
["Cooling capacity","Nom.","","","kW","4.86 (1), 4.52 (2)","5.83 (1), 5.09 (2)","6.18 (1), 5.44 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Capacity control","Method","","","","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)"]
["Power input","Cooling","","Nom.","kW","0.820 (1), 1.36 (2)","1.08 (1), 1.55 (2)","1.19 (1), 1.73 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["EER","","","","","5.91 (1), 3.32 (2)","5.40 (1), 3.28 (2)","5.19 (1), 3.14 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["SEER","","","","","","","","5.79 (5)","5.71 (5)","5.59 (5)"]
["Dimensions","Unit","","Depth","mm","362","362","362","460","460","460"]
["","","","Height","mm","770","770","770","870","870","870"]
["","","","Width","mm","1250","1250","1250","1380","1380","1380"]
["Weight","Unit","","","kg","88","88","88","147","147","147"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Zinc coated low carbon steel","Zinc coated low carbon steel","Zinc coated low carbon steel","Polyester painted galvanised steel plate","Polyester painted galvanised steel plate","Polyester painted galvanised steel plate"]
["Air heat exchanger","Type","","","","","","","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler"]
["Fan","Quantity","","","","1","1","1","1","1","1"]
["","Type","","","","Propeller fan","Propeller fan","Propeller fan","Propeller fan","Propeller fan","Propeller fan"]
["Fan motor","Drive","","","","","","","Direct drive","Direct drive","Direct drive"]
["Compressor","Quantity","","","","1","1","1","1","1","1"]
["","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing inverter compressor","Hermetically sealed swing inverter compressor","Hermetically sealed swing inverter compressor"]
["","Starting method","","","","","","","Inverter driven","Inverter driven","Inverter driven"]
["Operation range","Air side","Cooling","Min.","°CDB","10 (3)","10 (3)","10 (3)","10","10","10"]
["","","","Max.","°CDB","43","43","43","43","43","43"]
["","Water side","Evaporator","Min.","°CDB","5 (3)","5 (3)","5 (3)","5","5","5"]
["","","","Max.","°CDB","22","22","22","22","22","22"]
["Sound power level","Cooling","","Nom.","dBA","61","62","62","67.0","69.0","69.0"]
["Sound pressure level","Cooling","","Nom.","dBA","48","49","50","47.7","50.8","51.0"]
["Refrigerant","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32"]
["","GWP","","","","675","675","675","675.0","675.0","675.0"]
["","Charge","","","kg","1.35","1.35","1.35"]
["","Circuits","","Quantity","","","","","1","1","1"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","230 +/-10%","230 +/-10%","230 +/-10%","230","230","230"]
["","Voltage range","","Min.","%","","","","-10","-10","-10"]
["","","","Max.","%","","","","10","10","10"]
["Unit","Running current","","Max","A","","","","30.8","30.8","30.8"]
["Notes","","","","","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB"]
["","","","","","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB"]
["","","","","","(3) - For more details, see operation range drawing","(3) - For more details, see operation range drawing","(3) - For more details, see operation range drawing","(3) - According to EN14825","(3) - According to EN14825","(3) - According to EN14825"]
["","","","","","","","","(4) - Depends on operation mode, refer to installation manual.","(4) - Depends on operation mode, refer to installation manual.","(4) - Depends on operation mode, refer to installation manual."]