{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":13,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZSRC2"]
[]
[]
[]
[]
["","","","","","EWADH11TZSRC2","EWADH18TZSRC2","EWADH19TZSRC2","EWADH13TZSRC2","EWADH12TZSRC2","EWADC16TZSRC2","EWADH17TZSRC2","EWADC15TZSRC2"]
["Cooling capacity","Nom.","","","kW","1,164","1,812","1,876","1,323","1,229","1,595","1,712","1,463"]
["Capacity control","Method","","","","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Power input","Cooling","","Nom.","kW","384.6","663.5","741.2","446","423.1","564.5","611.2","513.9"]
["EER","","","","","3.03","2.73","2.53","2.97","2.91","2.83","2.80","2.85"]
["IPLV","","","","","5.43","5.51","5.36","5.34","5.29","5.53","5.5","5.53"]
["SEER","","","","","5.24","5.20","5.11","5.15","5.12","5.21","5.20","5.18"]
["Dimensions","Unit","","Depth","mm","10,510","14,102","14,102","11,404","10,510","12,302","13,202","11,404"]
["","","","Height","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Width","mm","2,282","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["Weight","Operation weight","","","kg","9,879","13,048","13,048","11,123","9,879","12,145","12,575","11,727"]
["","Unit","","","kg","9,322","12,037","12,037","10,112","9,322","11,134","11,564","10,716"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Air heat exchanger","Type","","","","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel"]
["Fan","Quantity","","","","22","30","30","24","22","26","28","24"]
["","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller"]
["Fan motor","Drive","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven"]
["Compressor","Quantity","","","","2","2","2","2","2","2","2","2"]
["","Type","","","","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor"]
["","Starting method","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven"]
["Sound power level","Cooling","","Nom.","dBA","93","96","96","94","93","94","95","94"]
["Sound pressure level","Cooling","","Nom.","dBA","70","72","73","71","71","71","72","71"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","175","270","270","200","175","220","250","200"]
["","Circuits","","Quantity","","2","2","2","2","2","2","2","2"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","219.1mm","273mm","273mm","273mm","219.1mm","273mm","273mm","273mm"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400"]
["","Voltage range","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10"]
["Unit","Starting current","","Max","A","0","0","0","0","0","0","0","0"]
["","Running current","Cooling","Nom.","A","659.2","1,080","1,194","748.1","708.5","922.8","1,000","853.7"]
["","","","Max","A","913","1,398","1,487","1,027","969","1,205","1,301","1,165"]
["","Max unit current for wires sizing","","","A","1,004","1,538","1,636","1,130","1,066","1,326","1,431","1,282"]