{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":82,"n_cols":61,"rows_kept":82,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAT-B-XR"]
[]
[]
[]
[]
["","","","","","EWAT085B-XRA1","EWAT085B-XRB1","EWAT115B-XRA1","EWAT115B-XRB1","EWAT145B-XRA1","EWAT145B-XRB1","EWAT180B-XRA2","EWAT180B-XRB2","EWAT185B-XRA1","EWAT185B-XRB1","EWAT200B-XRA2","EWAT200B-XRB2","EWAT220B-XRA2","EWAT220B-XRB2","EWAT230B-XRA1","EWAT230B-XRB1","EWAT250B-XRA2","EWAT250B-XRB2","EWAT250B-XRC1","EWAT280B-XRA2","EWAT280B-XRB2","EWAT300B-XRA1","EWAT300B-XRB1","EWAT310B-XRA2","EWAT310B-XRB2","EWAT320B-XRA2","EWAT320B-XRB2","EWAT320B-XRC1","EWAT360B-XRA1","EWAT360B-XRB1","EWAT370B-XRA2","EWAT370B-XRB2","EWAT370B-XRC1","EWAT390B-XRC2","EWAT430B-XRA2","EWAT430B-XRB2","EWAT450B-XRC2","EWAT470B-XRA2","EWAT470B-XRB2","EWAT510B-XRC2","EWAT540B-XRA2","EWAT540B-XRB2","EWAT540B-XRC2","EWAT590B-XRC2","EWAT600B-XRA2","EWAT600B-XRB2","EWAT630B-XRC2","EWAT660B-XRA2","EWAT660B-XRB2","EWAT700B-XRA2","EWAT700B-XRB2","EWAT720B-XRC2","EWAT760B-XRC2","EWAT830B-XRC2","EWAT880B-XRC2","EWATC10B-XRC2"]
["Sound pressure level","Cooling","","Nom.","dBA","60.2","60.2 (1)","63.9","63.9 (1)","65.6","65.6 (1)","65.3","65.3 (1)","67.7","67.7 (1)","65.5","65.5 (1)","65.8","65.8 (1)","66.7","66.7 (1)","66.3","66.3 (1)","64.9","67.1","67.1 (1)","67.5","67.5 (1)","67.2","67.2 (1)","67.4","67.4 (1)","65.7","67.8","67.8 (1)","67.7","67.7 (1)","66.0","65.9","68.3","68.3 (1)","66.5","68.5","68.5 (1)","66.7","68.9","68.9 (1)","66.9","67.1","69.2","69.2 (1)","67.2","69.3","69.3 (1)","69.6","69.6 (1)","67.5","67.6","67.7","67.8","68.1"]
["Operation range","Air side","Cooling","Min.","°CDB","-10","","-10","","-10","","-18","","-10","","-18","","-18","","-18","","-18","","","-18","","-18","","-18","","-18","","","-18","","-18","","","","-18","","","-18","","","-18","","","","-18","","","-18","","-18"]
["","","","Max.","°CDB","46","","46","","46","","46","","46","","46","","46","","46","","46","","","46","","46","","46","","46","","","46","","46","","","","46","","","46","","","46","","","","46","","","46","","46"]
["","Water side","Cooling","Max.","°CDB","20","","20","","20","","20","","20","","20","","20","","20","","20","","","20","","20","","20","","20","","","20","","20","","","","20","","","20","","","20","","","","20","","","20","","20"]
["","","","Min.","°CDB","-13","","-13","","-13","","-13","","-13","","-13","","-13","","-13","","-13","","","-13","","-13","","-13","","-13","","","-13","","-13","","","","-13","","","-13","","","-13","","","","-13","","","-13","","-13"]
["Compressor","Type","","","","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Driven vapour compression","Scroll compressor","Driven vapour compression","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor"]
["","Starting method","","","","","Direct on line","","Direct on line","","Direct on line","","","","Direct on line","","Direct on line","","Direct on line","","Direct on line","","Direct on line","","","Direct on line","","Direct on line","","","","Direct on line","","","Direct on line","","Direct on line","","","","Direct on line","","","Direct on line","","","Direct on line","","","","Direct on line","","","Direct on line","","Direct on line"]
["","Quantity","","","","2","2","2","2","2","2","4","4","2","2","4","4","4","4","2","2","4","4","2","4","4","3","3","4","4","4","4","3","3","3","4","4","3","4","4","4","4","4","4","4","5","5","5","5","6","6","5","6","6","6","6","6","6","7","7","8"]
["Weight","Operation weight","","","kg","752","752","846","846","968","968","1,743","1,747","1,088","1,088","1,773","1,777","1,801","1,813","1,997","2,098","2,066","2,104","2,045","2,209","2,250","2,234","2,338","2,241","2,281","2,277","2,318","2,577","2,614","2,751","2,655","2,821","2,698","2,780","2,848","2,916","3,324","3,268","3,421","3,538","3,497","3,675","4,003","4,115","3,916","4,148","4,223","4,290","4,550","4,432","4,692","4,801","4,909","5,697","5,806","6,549"]
["","Unit","","","kg","744","747","837","840","961","959","1,732","1,736","1,072","1,076","1,763","1,766","1,790","1,802","1,977","2,082","2,054","2,090","2,020","2,192","2,231","2,212","2,318","2,220","2,262","2,247","2,299","2,550","2,590","2,731","2,627","2,801","2,670","2,740","2,811","2,888","3,290","3,237","3,393","3,480","3,458","3,633","3,940","4,060","3,873","4,106","4,160","4,248","4,500","4,396","4,642","4,720","4,830","5,620","5,730","6,450"]
["Air heat exchanger","Type","","","","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel"]
["EER","","","","","2.64","2.66","2.78","2.79","2.88","2.89","2.84","2.84","2.35","2.36","2.68","2.69","2.58","2.58","2.83","2.84","2.76","2.73","2.977","2.87","2.87","2.71","2.72","2.76","2.76","2.63","2.63","3.135","2.7","2.71","2.66","2.67","2.929","2.869","2.68","2.69","3.052","2.68","2.69","3.019","2.66","2.64","3.262","3.119","2.74","2.76","2.990","2.76","2.77","2.71","2.72","3.107","3.003","3.067","2.979","2.985"]
["ESEER","","","","","4.02","","4.18","","4.08","","4.24","","4.04","","4.21","","4.17","","4.16","","4.15","","","4.34","","4.31","","4.12","","4.04","","","4.24","","4.15","","","","4.15","","","4.12","","","4.2","","","","4.21","","","4.25","","4.23"]
["Refrigerant","GWP","","","","675","","675","","675","","675","675","675","","675","","675","","675","","675","","","675","","675","","675","675","675","","","675","","675","","","","675","","","675","","","675","","","","675","","","675","","675"]
["","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Circuits","","Quantity","","1","","1","","1","","2","2","1","","2","","2","","1","","2","","","2","","1","","2","2","2","","","1","","2","","","","2","","","2","","","2","","","","2","","","2","","2"]
["","Charge","","","kg","10.5","8.4","12.5","9.1","15","10.3","30","12","16","11.8","36","19.1","37","18.9","30","22.7","42","22.5","44.0","48","28.7","36","27.3","50","28","52","26.6","50.0","50","30","58","33.2","55.0","30.5","62","35","30.5","70","40.9","39.5","78","48.2","42.0","45.0","80","51.5","49.0","92","59.2","100","62","55.0","57.5","62.5","67.0","75.0"]
["Cooling capacity","Nom.","","","kW","81.68","82","108.36","109","135.38","136","167.75","168","165.77","166","187.07","188","207.97","208","223.94","225","238.24","238","241.40","264.17","265","284.03","285","283.97","285","301.05","302","313.20","327.53","329","345.32","346","355.68","370.32","393.29","394","431.43","437.99","440","489.48","500","502","520.68","563.54","569.48","572","603.94","618.9","621","656.69","659","687.57","729.00","800.94","842.34","965.50"]
["Water heat exchanger","Water volume","","","l","5","","6","","9","","11","11","12","","11","","11","","16","","14","","","19","","20","","19","19","19","","","20","","20","","","","28","","","28","","","42","","","","42","","","50","","50"]
["","Type","","","","Brazed plate","","Brazed plate","","Brazed plate","","Brazed plate","Brazed plate","Brazed plate","","Brazed plate","","Brazed plate","","Brazed plate","","Brazed plate","","","Brazed plate","","Brazed plate","","Brazed plate","Brazed plate","Brazed plate","","","Brazed plate","","Brazed plate","","","","Brazed plate","","","Brazed plate","","","Brazed plate","","","","Brazed plate","","","Brazed plate","","Brazed plate"]
["Power input","Cooling","","Nom.","kW","30.9","","39","","47","","59.1","59.1","70.5","","69.8","","80.7","","79.2","","86.4","","","92.2","","104","","103","103","114","","","121","","130","","","","146","","","163","","","188","","","","207","","","224","","242"]
["Sound power level","Cooling","","Nom.","dBA","77.9","77.9 (1)","81.9","81.9 (1)","84","84 (1)","84.2","84.2 (1)","86","86 (1)","84.5","84.5 (1)","84.8","84.8 (1)","86.2","86.2 (1)","85.8","85.8 (1)","84.0","86.6","86.6 (1)","87","87 (1)","86.7","86.7 (1)","86.9","86.9 (1)","85.4","87.7","87.7 (1)","87.6","87.6 (1)","85.7","85.6","88.3","88.3 (1)","86.8","88.9","88.9 (1)","87.0","89.3","89.3 (1)","87.6","87.8","90","90 (1)","87.9","90.4","90.4 (1)","90.7","90.7 (1)","88.6","88.7","89.3","89.4","90.0"]
["Dimensions","Unit","","Width","mm","1,204","1,204","1,204","1,204","1,204","1,204","2,236","2,236","1,204","1,204","2,236","2,236","2,236","2,236","2,236","2,236","2,236","2,236","2,238","2,236","2,236","2,236","2,236","2,236","2,236","2,236","2,236","2,238","2,236","2,236","2,236","2,236","2,238","2,238","2,236","2,236","2,238","2,236","2,236","2,238","2,236","2,236","2,238","2,238","2,236","2,236","2,238","2,236","2,236","2,236","2,236","2,238","2,238","2,238","2,238","2,238"]
["","","","Depth","mm","2,660","2,660","3,180","3,180","3,780","3,780","2,326","2,326","3,780","3,780","2,326","2,326","2,326","2,326","3,226","3,226","3,226","3,226","2,510","3,226","3,226","3,226","3,226","3,226","3,226","3,226","3,226","53,600","4,126","4,126","4,126","4,126","3,590","3,590","4,126","4,126","4,670","5,025","5,025","4,670","5,025","5,025","5,750","5,750","5,874","5,874","5,750","6,774","6,774","6,774","6,774","6,830","6,830","8,010","8,010","9,090"]
["","","","Height","mm","1,801","1,801","1,801","1,801","1,822","1,822","2,540","2,540","1,822","1,822","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,535","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,535","2,540","2,540","2,540","2,540","2,535","2,535","2,540","2,540","2,535","2,540","2,540","2,535","2,540","2,540","2,535","2,535","2,540","2,540","2,535","2,540","2,540","2,540","2,540","2,535","2,535","2,535","2,535","2,535"]
["Capacity control","Minimum capacity","","","%","50","50","38","38","50","50","25","25","38","38","21","21","19","19","50","50","17","17","50","16","16","24","24","14","14","22","22","22","33","33","19","19","19","18","17","17","16","25","25","25","14","14","14","22","12","12","20","11","11","17","17","18","17","15","14","25"]
["","Method","","","","Staged","Step","Staged","Step","Staged","Step","Variable","Step","Staged","Step","Variable","Step","Variable","Step","Staged","Step","Variable","Step","Step","Variable","Step","Variable","Step","Variable","Step","Variable","Step","Step","Variable","Step","Variable","Step","Step","Step","Variable","Step","Step","Variable","Step","Step","Variable","Step","Step","Step","Variable","Step","Step","Variable","Step","Variable","Step","Step","Step","Step","Step","Step"]
["Water heat exchanger - evaporator","Water pressure drop","Cooling","Nom.","kPa","","","","","","","","","","","","","","","","","","","31.24","","","","","","","","","51.60","","","","","58.41","55.59","","","74.92","","","16.26","","","18.26","21.17","","","24.12","","","","","20.74","23.17","27.72","30.55","31.46"]
["","Water volume","","","l","","","","","","","","","","","","","","","","","","","23","","","","","","","","","23","","","","","27","35","","","35","","","59","","","59","59","","","59","","","","","76","76","76","76","92"]
["Fan","Air flow rate","","Nom.","l/s","6,673","","8,896","","11,122","","15,054","15,054","11,122","","15,054","","15,054","","18,819","","18,818","","","22,582","","22,582","","22,582","22,582","22,582","","","26,346","","26,346","","","","30,110","","","33,874","","","37,637","","","","45,164","","","48,928","","52,692"]
["","","Cooling","Nom.","l/s","","","","","","","","","","","","","","","","","","","18,900","","","","","","","","","28,350","","","","","28,350","28,350","","","37,800","","","37,800","","","47,250","47,250","","","47,250","","","","","56,700","56,700","66,150","66,150","75,600"]
["","Speed","","","rpm","1,108","","1,108","","1,108","","700","700","1,108","","700","","700","","700","","700","","","700","","700","","700","700","700","","","700","","700","","","","700","","","700","","","700","","","","700","","","700","","700"]
["Compressor","Starting method","","","","Direct on line","","Direct on line","","Direct on line","","Direct on line","Direct on line","Direct on line","","Direct on line","","Direct on line","","Direct on line","","Direct on line","","","Direct on line","","Direct on line","","Direct on line","Direct on line","Direct on line","","","Direct on line","","Direct on line","","","","Direct on line","","","Direct on line","","","Direct on line","","","","Direct on line","","","Direct on line","","Direct on line"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Voltage range","","Max.","%","","10","","10","","10","","","","10","","10","","10","","10","","10","10","","10","","10","","","","10","10","","10","","10","10","10","","10","10","","10","10","","10","10","10","","10","10","","10","","10","10","10","10","10","10"]
["","","","Min.","%","","-10","","-10","","-10","","","","-10","","-10","","-10","","-10","","-10","0","","-10","","-10","","","","-10","0","","-10","","-10","0","0","","-10","0","","-10","0","","-10","0","0","","-10","0","","-10","","-10","0","0","0","0","0"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","","400","","400","","400","","400","","400","","400","","400","","400","","400","400","","400","","400","","400","","400","400","","400","","400","400","400","","400","400","","400","400","","400","400","400","","400","400","","400","","400","400","400","400","400"]
["Unit","Max unit current for wires sizing","","","A","","79","","109","","108","","","","178","","182","","210","","184","","209","219","","253","","267","","","","278","280","","275","","285","327","332","","358","390","","365","437","","449","451","498","","534","545","","542","","549","606","653","763","763","871"]
["","Starting current","","Max","A","","215","","315","","328","","","","464","","388","","399","","506","","414","647","","543","","554","","","","564","703","","592","","602","746","750","","640","803","","678","845","","727","858","901","","779","944","","817","","855","999","1,042","1,142","1,142","1,240"]
["","Running current","Cooling","Nom.","A","","59","","71","","83","","","","118","","128","","143","","134","","151","143","","164","","177","","","","194","178","","204","","221","213","225","","250","249","","276","286","","319","287","322","","352","356","","381","","410","393","428","463","498","570"]
["","","","Max","A","","75","","87","","100","","","","134","","160","","171","","176","","186","199","","213","","224","","","","235","255","","262","","273","298","302","","311","355","","348","397","","397","410","453","","449","496","","487","","525","551","594","694","694","792"]
["Notes","","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0"]
["","","","","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only","(2) - In accordance with standard EN14825:2013 comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281","(2) - The value refers to the pressure drop in the evaporator only"]
["","","","","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1"]
["","","","","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level.","(4) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(4) - The certification refers only to the overall sound power level."]
["","","","","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(5) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(5) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding"]
["","","","","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - All data refers to the standard unit without options.","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition"]
["","","","","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - All data are subject to change without notice. Please refer to the unit nameplate data.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request."]
["","","","","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water","(8) - The value refers to the pressure drop in the evaporator only","(8) - Fluid: Water"]
["","","","","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(9) - Option FANMOD consist in Continuous Fan Speed Regulation and improves part load operation. Single-V units are standardly equipped with continuous fan control, Multi-V units require opt 99 - VFD fans","(9) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(10) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(10) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(11) - In case of inverter driven units, no inrush current at start up is experienced.","(11) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current"]
["","","","","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(12) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(12) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current."]
["","","","","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(13) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(13) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(14) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(14) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options.","(15) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(15) - The data are referred to the unit without additional options."]
["","","","","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(16) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book"]
["Space cooling","ηs,c","","","%","","213.28","","179.4","","166.6","","","","164.6","","186.6","","179","","169","","177","","","186.6","","185.8","","","","173.8","","","180.6","","176.2","","","","181.8","","","179","","","183","","","","187.4","","","187.4","","185.4"]
["Refrigerant","GWP","","","","","675","","675","","675","","","","675","","675","","675","","675","","675","675","","675","","675","","","","675","675","","675","","675","675","675","","675","675","","675","675","","675","675","675","","675","675","","675","","675","675","675","675","675","675"]
["","Circuits","","Quantity","","","1","","1","","1","","","","1","","2","","2","","1","","2","1","","2","","1","","","","2","1","","1","","2","1","2","","2","2","","2","2","","2","2","2","","2","2","","2","","2","2","2","2","2","2"]
["Fan motor","Drive","","","","","Phase cut","","Phase cut","","Phase cut","","","","Phase cut","","VFD driven","","VFD driven","","VFD driven","","VFD driven","ON/OFF","","VFD driven","","VFD driven","","","","VFD driven","ON/OFF","","VFD driven","","VFD driven","ON/OFF","ON/OFF","","VFD driven","ON/OFF","","VFD driven","ON/OFF","","VFD driven","ON/OFF","ON/OFF","","VFD driven","ON/OFF","","VFD driven","","VFD driven","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF"]
["IPLV","","","","","","4.74","","5.1","","4.76","","","","4.72","","5.05","","4.97","","4.86","","4.91","5.340","","5.08","","4.78","","","","4.62","5.525","","5.04","","4.95","5.487","5.317","","4.88","5.446","","4.72","5.528","","4.96","5.630","5.620","","5.04","5.601","","5.07","","5.08","5.649","5.605","5.613","5.605","5.576"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","","76.1","","76.1","","76.1","","","","76.1","","88.9","","88.9","","76.1","","88.9","88.9mm","","88.9","","76.1","","","","88.9","88.9mm","","76.1","","88.9","88.9mm","88.9mm","","88.9","88.9mm","","88.9","139.7mm","","114.3","139.7mm","139.7mm","","114.3","139.7mm","","114.3","","114.3","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm"]
["SEER","","","","","","4.13","","4.56","","4.24","","","","4.19","","4.74","","4.55","","4.3","","4.5","4.965","","4.74","","4.72","","","","4.42","5.186","","4.59","","4.48","5.140","4.979","","4.62","5.158","","4.55","5.108","","4.65","5.279","5.270","","4.76","5.237","","4.76","","4.71","5.291","5.249","5.324","5.294","5.229"]
["Power input","Cooling","","Nom.","kW","","30.8","","38.9","","46.9","","","","70.5","","69.8","","80.7","","79.2","","87.3","81.1","","92.2","","105","","","","115","99.9","","121","","130","121.4","129.1","","147","141.4","","163","162.1","","190","159.6","180.7","","207","202.0","","224","","242","221.3","242.8","261.1","282.2","323.5"]
["Casing","Material","","","","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["","Colour","","","","","Ivory white","","Ivory white","","Ivory white","","","","Ivory white","","Ivory white","","Ivory white","","Ivory white","","Ivory white","Ivory white","","Ivory white","","Ivory white","","","","Ivory white","Ivory white","","Ivory white","","Ivory white","Ivory white","Ivory white","","Ivory white","Ivory white","","Ivory white","Ivory white","","Ivory white","Ivory white","Ivory white","","Ivory white","Ivory white","","Ivory white","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["Fan","Type","","","","","Direct propeller","","Direct propeller","","Direct propeller","","","","Direct propeller","","Direct propeller","","Direct propeller","","Direct propeller","","Direct propeller","Direct propeller","","Direct propeller","","Direct propeller","","","","Direct propeller","Direct propeller","","Direct propeller","","Direct propeller","Direct propeller","Direct propeller","","Direct propeller","Direct propeller","","Direct propeller","Direct propeller","","Direct propeller","Direct propeller","Direct propeller","","Direct propeller","Direct propeller","","Direct propeller","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller"]
["","Quantity","","","","","6","","8","","10","","","","10","","4","","4","","5","","5","4","","6","","6","","","","6","6","","7","","7","6","6","","8","8","","9","8","","10","10","10","","12","10","","13","","14","12","12","14","14","16"]
["Notes","","","","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data.","","(17) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["Water heat exchanger - evaporator","Type","","","","","","","","","","","","","","","","","","","","","","Brazed plate","","","","","","","","","Brazed plate","","","","","Brazed plate","Brazed plate","","","Brazed plate","","","Brazed plate","","","Brazed plate","Brazed plate","","","Brazed plate","","","","","Brazed plate","Brazed plate","Brazed plate","Brazed plate","Brazed plate"]
["Operation range","Air side","Cooling","Min.","°CDB","","","","","","","","","","","","","","","","","","","-20","","","","","","","","","-20","","","","","-20","-20","","","-20","","","-20","","","-20","-20","","","-20","","","","","-20","-20","-20","-20","-20"]
["","","","Max.","°CDB","","","","","","","","","","","","","","","","","","","52","","","","","","","","","52","","","","","52","52","","","52","","","52","","","52","52","","","52","","","","","52","52","52","52","52"]
["","Water side","Evaporator","Min.","°CDB","","","","","","","","","","","","","","","","","","","-13","","","","","","","","","-13","","","","","-13","-13","","","-13","","","-13","","","-13","-13","","","-13","","","","","-13","-13","-13","-13","-13"]
["","","","Max.","°CDB","","","","","","","","","","","","","","","","","","","30","","","","","","","","","30","","","","","30","30","","","30","","","30","","","30","30","","","30","","","","","30","30","30","30","30"]