{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":53,"n_cols":16,"rows_kept":53,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWHQ-G-SS"]
[]
[]
[]
[]
["","","","","","EWHQ100G-SS","EWHQ120G-SS","EWHQ130G-SS","EWHQ150G-SS","EWHQ160G-SS","EWHQ190G-SS","EWHQ210G-SS","EWHQ240G-SS","EWHQ270G-SS","EWHQ340G-SS","EWHQ400G-SS"]
["Cooling capacity","Nom.","","","kW","87.3","100.0","111","127","141","160","181","208","232","291","352"]
["Heating capacity","Nom.","","","kW","112","128","144","162","179","205","233","266","299","375","454"]
["Capacity control","Method","","","","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step"]
["","Minimum capacity","","","%","50.0","43.0","50.0","44.0","50.0","45.0","50.0","43.0","50.0","40.0","50.0"]
["Power input","Cooling","","Nom.","kW","22.4","25.3","28.5","32.0","35.6","41.1","46.0","53.3","59.1","73.7","88.4"]
["","Heating","","Nom.","kW","27.0","30.9","35.2","39.3","43.6","50.4","56.6","64.7","72.2","90.3","109"]
["EER","","","","","3.90","3.95","3.91","3.96","3.95","3.90","3.93","3.90","3.92","3.95","3.98"]
["COP","","","","","4.15","4.16","4.09","4.12","4.11","4.07","4.11","4.10","4.14","4.16","4.18"]
["ESEER","","","","","4.70","4.84","4.65","4.86","4.80","4.89","4.86","4.83","4.79","4.90","4.83"]
["Dimensions","Unit","","Depth","mm","2432","2432","2264","2264","2264","2432","2432","2432","2432","2432","2432"]
["","","","Height","mm","1066","1066","1066","1066","1066","1066","1066","1066","1066","1186","1186"]
["","","","Width","mm","928","928","928","928","928","928","928","928","928","928","928"]
["Weight","Unit","","","kg","519","608","728","770","808","838","880","930","941","1090","1203"]
["","Operation weight","","","kg","558","654","782","830","873","908","995","1019","1031","1202","1334"]
["Water heat exchanger - evaporator","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water volume","","","l","6","8","8","10","12","13","15","17","17","27","34"]
["Water heat exchanger - condenser","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["Compressor","Type","","","","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor"]
["","Quantity","","","","2","2","2","2","2","2","2","2","2","2","2"]
["Sound power level","Cooling","","Nom.","dBA","80","83","85","87","88","88","88","90","92","93","93"]
["Sound pressure level","Cooling","","Nom.","dBA","64","67","69","70","72","72","72","74","76","76","77"]
["Operation range","Evaporator","Cooling","Min.","°CDB","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8"]
["","","","Max.","°CDB","15","15","15","15","15","15","15","15","15","15","15"]
["","Condenser","Cooling","Min.","°CDB","25","25","25","25","25","25","25","25","25","25","25"]
["","","","Max.","°CDB","55","55","55","55","55","55","55","55","55","55","55"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["","Circuits","","Quantity","","1","1","1","1","1","1","1","1","1","1","1"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["Refrigerant charge","Per circuit","","","kg","9.0","9.0","10.0","10.0","13.0","11.0","13.0","15.0","15.0","19.0","19.0"]
["","Per circuit","","","tCO2Eq","18.8","18.8","20.9","20.9","27.1","23.0","27.1","31.3","31.3","39.7","39.7"]
["Space heating","Average climate water outlet 35°C","General","SCOP","","4.08","4.08","4.14","4.24","4.23","4.23","4.22","4.37","4.35","4.16"]
["Energy Efficiency Range","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation."]
["","","","","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation"]
["","","","","","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units"]
["","","","","","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water"]
["","","","","","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["","","","","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load"]
["","","","","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current"]
["","","","","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1"]