{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":27,"n_cols":11,"rows_kept":27,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWLH-J-SS"]
[]
[]
[]
[]
["","","","","EWLH080J-SS","EWLH100J-SS","EWLH110J-SS","EWLH130J-SS","EWLH140J-SS","EWLH170J-SS","EWLH190J-SS"]
["Sound pressure level","Cooling","Nom.","dBA","79","79","79","79","79","79","79"]
["Refrigerant","Circuits","Quantity","","1","1","1","1","1","1","1"]
["","Type","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["Cooling capacity","Nom.","","kW","84","102","109","127","142","174","193"]
["Power input","Cooling","Nom.","kW","23.3","28.1","31.8","37","41.5","49.6","56.3"]
["Sound power level","Cooling","Nom.","dBA","88.9","88.9","88.9","88.9","88.9","88.9","88.9"]
["Dimensions","Unit","Width","mm","913","913","913","913","913","913","913"]
["","","Depth","mm","2,684","2,684","2,684","2,684","2,684","2,684","2,684"]
["","","Height","mm","1,020","1,020","1,020","1,020","1,020","1,020","1,020"]
["Compressor","Type","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Quantity","","","1","1","1","1","1","1","1"]
["Capacity control","Minimum capacity","","%","25","25","25","25","25","25","25"]
["","Method","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Weight","Operation weight","","kg","1,138","1,159","1,253","1,281","1,327","1,518","1,518"]
["","Unit","","kg","1,124","1,141","1,237","1,263","1,305","1,489","1,489"]
["Water heat exchanger - evaporator","Type","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water volume","","l","14","18","14","17","20","26","26"]
["EER","","","","3.62","3.62","3.43","3.42","3.43","3.51","3.43"]
["Power supply","Phase","","","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","V","400","400","400","400","400","400","400"]