{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":57,"n_cols":21,"rows_kept":57,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWD-J-SS"]
[]
[]
[]
[]
["","","","","","EWWD120J-SS","EWWD140J-SS","EWWD150J-SS","EWWD180J-SS","EWWD210J-SS","EWWD250J-SS","EWWD280J-SS","EWWD310J-SS","EWWD330J-SS","EWWD360J-SS","EWWD380J-SS","EWWD400J-SS","EWWD450J-SS","EWWD500J-SS","EWWD530J-SS","EWWD560J-SS"]
["Cooling capacity","Nom.","","","kW","119.7","145.7","154.3","177.3","207.3","255.3","284.1","309 (1)","333 (1)","356 (1)","385 (1)","415 (1)","463 (1)","512 (1)","540 (1)","568 (1)"]
["Heating capacity","Nom.","","","kW","144.2","175.4","189.8","217.8","252.2","308.4","347.4","388 (2)","417 (2)","446 (2)","486 (2)","515 (2)","573 (2)","631 (2)","669 (2)","709 (2)"]
["Capacity control","Method","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["","Minimum capacity","","","%","25","25","25","25","25","25","25","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Power input","Cooling","","Nom.","kW","28","34","39.5","45.3","50.4","59.9","70","78.8 (1)","84.6 (1)","90.3 (1)","101 (1)","101 (1)","110 (1)","120 (1)","130 (1)","140 (1)"]
["","Heating","","Nom.","kW","27.7","33.7","39.2","44.9","50.1","59.7","69.7","78.8 (2)","84.6 (2)","90.3 (2)","101 (2)","101 (2)","110 (2)","120 (2)","130 (2)","140 (2)"]
["EER","","","","","4.28","4.28","3.91","3.92","4.11","4.26","4.06","3.92 (1)","3.94 (1)","3.94 (1)","3.82 (1)","4.12 (1)","4.20 (1)","4.28 (1)","4.16 (1)","4.05 (1)"]
["COP","","","","","5.2","5.2","4.84","4.85","5.04","5.17","4.98","4.92 (2)","4.94 (2)","4.94 (2)","4.82 (2)","5.12 (2)","5.20 (2)","5.28 (2)","5.16 (2)","5.05 (2)"]
["ESEER","","","","","","","","","","","","4.32","4.35","4.50","4.31","4.65","4.74","4.83","4.73","4.33"]
["Dimensions","Unit","","Depth","mm","2684","2684","2684","2684","2684","2684","2684","2684","2684","2684","2684","2684","2684","2684","2684","2684"]
["","","","Height","mm","1020","1020","1020","1020","1020","1020","1020","2000","2000","2000","2000","2000","2000","2000","2000","2000"]
["","","","Width","mm","913","913","913","913","913","913","913","913","913","913","913","913","913","913","913","913"]
["Weight","Unit","","","kg","1177","1233","1334","1366","1416","1600","1607","2668","2700","2732","2782","2832","3016","3200","3207","3215"]
["","Operation weight","","","kg","1211","1276","1378","1415","1473","1663","1675","2755","2792","2830","2888","2946","3136","3327","3338","3350"]
["Water heat exchanger - evaporator","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water volume","","","l","14","18","14","17","20","26","26","29","31","33","37","41","46","52","52","52"]
["","Water flow rate","","Nom.","l/s","5.7","7","7.4","8.5","9.9","12.2","13.6","14.8","15.9","17.0","18.4","19.8","22.1","24.5","25.8","27.2"]
["Water heat exchanger - condenser","Type","","","","","","","","","","","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube"]
["","Water flow rate","","Nom.","l/s","","","","","","","","9.3","9.3","10.7","11.0","12.4","12.4","15.2","15.3","17.0"]
["Compressor","Type","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Quantity","","","","1","1","1","1","1","1","1","2","2","2","2","2","2","2","2","2"]
["Sound power level","Cooling","","Nom.","dBA","95.0","95.0","95.0","95.0","95.0","95.0","95.0","94","94","94","94","94","94","94","94","94"]
["Sound pressure level","Cooling","","Nom.","dBA","79.0","79.0","79.0","79.0","79.0","79.0","79.0","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)"]
["Operation range","Evaporator","Cooling","Min.","°CDB","","","","","","","","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","","","","","","","","15","15","15","15","15","15","15","15","15"]
["","Condenser","Cooling","Min.","°CDB","","","","","","","","23","23","23","23","23","23","23","23","23"]
["","","","Max.","°CDB","","","","","","","","60","60","60","60","60","60","60","60","60"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","Charge","","","kg","18","35","34","37","37","38","38"]
["","Circuits","","Quantity","","1","1","1","1","1","1","1","2","2","2","2","2","2","2","2","2"]
["","GWP","","","","1,430.0","1,430.0","1,430.0","1,430.0","1,430.0","1,430.0","1,430.0","1430","1430","1430","1430","1430","1430","1430","1430","1430"]
["Refrigerant charge","Per circuit","","","kg","","","","","","","","33.0","33.5","34.0","35.0","36.0","37.0","38.0","38.0","38.0"]
["","Per circuit","","","tCO2Eq","","","","","","","","47.2","47.9","48.6","50.1","51.5","52.9","54.3","54.3","54.3"]
["Space heating","Average climate water outlet 55°C","General","SCOP","","4.03","4.11","4.16","4.17","4.17","4.23","3.83"]
["","Average climate water outlet 35°C","General","SCOP","","","","","","","","","4.04"]
["Energy Efficiency Range","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation."]
["","","","","","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation"]
["","","","","","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744"]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load"]
["","","","","","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current"]
["","","","","","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","","","","","","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","","","","","","","","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","","","","","","","","","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water"]
["","","","","","","","","","","","","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","","","","","","","","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]