{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":16,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWQ-G-SS"]
[]
[]
[]
[]
["","","","","","EWWQ090G-SS","EWWQ100G-SS","EWWQ120G-SS","EWWQ130G-SS","EWWQ150G-SS","EWWQ170G-SS","EWWQ190G-SS","EWWQ210G-SS","EWWQ240G-SS","EWWQ300G-SS","EWWQ360G-SS"]
["Sound pressure level","Cooling","","Nom.","dBA","64","67","69","70","72","72","72","74","76","76","77"]
["Refrigerant","Circuits","","Quantity","","1","1","1","1","1","1","1","1","1","1","1"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","10","10","11","11","12","12","15","16","17","19","20"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Operation range","Condenser","Cooling","Min.","°CDB","25"]
["","","","Max.","°CDB","55"]
["","Evaporator","Cooling","Min.","°CDB","-10"]
["","","","Max.","°CDB","15"]
["Cooling capacity","Nom.","","","kW","93.7","105.6","119","135.9","150","172.1","193.8","220.7","246.1","314.3","370.4"]
["Power input","Cooling","","Nom.","kW","21.3","24","26.9","30.5","33.9","38.9","43.8","50.74","56.1","70.2","84"]
["Sound power level","Cooling","","Nom.","dBA","80","83","85","87","88","88","88","90","92","93","93"]
["Refrigerant charge","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","20.88","20.88","22.96","22.96","25.05","25.05","31.31","33.40","35.49","39.66","41.75"]
["Dimensions","Unit","","Width","mm","928","928","928","928","928","928","928","928","928","928","928"]
["","","","Depth","mm","2,432","2,432","2,264","2,264","2,264","2,432","2,432","2,432","2,432","2,432","2,432"]
["","","","Height","mm","1,066","1,066","1,066","1,066","1,066","1,066","1,066","1,066","1,066","1,186","1,186"]
["Compressor","Type","","","","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor"]
["","Quantity","","","","2","2","2","2","2","2","2","2","2","2","2"]
["Water heat exchanger - condenser","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water flow rate","","Nom.","l/s","5.52","6.23","7.05","8.04","8.87","10.17","11.43","13.02","14.53","18.46","21.81"]
["Capacity control","Minimum capacity","","","%","50","43","50","44","50","45","50","43","50","40","50"]
["","Method","","","","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed"]
["Weight","Operation weight","","","kg","554.9","652.4","781.6","821.4","859","901.4","945.9","1,009.6","1,023.2","1,194.7","1,311.1"]
["","Unit","","","kg","516","606","728","762","795","832","871","921","934","1,083","1,181"]
["Water heat exchanger - evaporator","Water flow rate","","Nom.","l/s","4.5","5.07","5.7","6.51","7.18","8.24","9.28","10.57","11.79","15.06","17.74"]
["","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water volume","","","l","6","8","8","10","12","13","15","17","17","27","34"]
["EER","","","","","4.399","4.4","4.424","4.456","4.425","4.424","4.425","4.349","4.387","4.477","4.41"]
["ESEER","","","","","5.51","5.52","5.51","5.53","5.51","5.53","5.52","5.52","5.52","5.52","5.52"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation."]
["","","","","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation"]
["","","","","","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(3) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units"]
["","","","","","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water","(4) - Fluid: Water"]
["","","","","","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(5) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(6) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["","","","","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load","(8) - Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load"]
["","","","","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current"]
["","","","","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1"]