{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":29,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWQ-L-SS"]
[]
[]
[]
[]
["","","","","EWWQ180L-SS","EWWQ180L-SS000","EWWQ205L-SS","EWWQ205L-SS000","EWWQ230L-SS","EWWQ230L-SS000","EWWQ260L-SS","EWWQ290L-SS","EWWQ290L-SS000","EWWQ330L-SS","EWWQ330L-SS000","EWWQ380L-SS","EWWQ380L-SS000","EWWQ430L-SS","EWWQ430L-SS000","EWWQ480L-SS000","EWWQ480L-SS","EWWQ540L-SS","EWWQ540L-SS000","EWWQ600L-SS","EWWQ600L-SS000","EWWQ660L-SS","EWWQ660L-SS000","EWWQ720L-SS","EWWQ720L-SS000"]
["Sound pressure level","Cooling","Nom.","dBA","65","","68","","70","","","74","","74","","73","","76","","","77","77","","78","","78","","78"]
["Refrigerant","Circuits","Quantity","","2","","2","","2","","","2","","2","","2","","2","","","2","2","","2","","2","","2"]
["","GWP","","","2,087.5","","2,087.5","","2,087.5","","","2,087.5","","2,087.5","","2,087.5","","2,087.5","","","2,087.5","2,087.5","","2,087.5","","2,087.5","","0"]
["","Charge","","kg","20","","20","","22","","","24","","24","","30","","32","","","34","34","","38","","40","","40"]
["","Type","","","R-410A","","R-410A","","R-410A","","","R-410A","","R-410A","","R-410A","","R-410A","","","R-410A","R-410A","","R-410A","","R-410A","","R-410A"]
["Cooling capacity","Nom.","","kW","187.4","","215.1","","244.3","","","303.2","","344.5","","386.8","","430.2","","","475.6","548.8","","610.9","","663","","721"]
["Power input","Cooling","Nom.","kW","41.7","","47.3","","53.1","","","67.1","","77.1","","87","","97.9","","","109.5","123.5","","139.7","","153.8","","166.9"]
["Sound power level","Cooling","Nom.","dBA","83","","86","","88","","","91","","91","","91","","93","","","95","95","","95","","96","","0"]
["Refrigerant charge","Refrigerant charge-=-Per circuit-=-TCO2Eq","","TCO2Eq","20.9","","20.9","","23.0","","","25.1","","25.1","","31.3","","33.4","","","35.5","35.5","","39.7","","41.8","","41.8"]
["Dimensions","Unit","Width","mm","928","","928","","928","","","928","","928","","928","","928","","","928","928","","928","","928","","928"]
["","","Depth","mm","2,801","","2,801","","2,801","","","2,801","","2,801","","2,801","","2,801","","","2,801","2,801","","2,801","","2,801","","2,801"]
["","","Height","mm","1,970","","1,970","","1,970","","","1,970","","1,970","","1,970","","1,970","","","1,970","2,090","","2,210","","2,210","","2,210"]
["Compressor","Type","","","Driven vapour compression","","Driven vapour compression","","Driven vapour compression","","","Driven vapour compression","","Driven vapour compression","","Driven vapour compression","","Driven vapour compression","","","Driven vapour compression","Driven vapour compression","","Driven vapour compression","","Driven vapour compression","","Driven vapour compression"]
["","Quantity","","","4","","4","","4","","","4","","4","","4","","4","","","4","4","","4","","4","","4"]
["Water heat exchanger - condenser","Type","","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","","Plate heat exchanger","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger"]
["","Water flow rate","Nom.","l/s","11.02","","12.66","","14.4","","","17.9","","20.38","","22.8","","25.4","","","28.08","32.3","","36.02","","39.16","","42.66"]
["Capacity control","Minimum capacity","","%","25","","21","","25","","","25","","23","","25","","21","","","25","22","","20","","18","","25"]
["","Method","","","Fixed","","Fixed","","Fixed","","","Fixed","","Fixed","","Fixed","","Fixed","","","Fixed","Fixed","","Fixed","","Fixed","","Fixed"]
["Weight","Operation weight","","kg","957","","1,156","","1,401","","","1,575","","1,641","","1,723","","1,851","","","1,918","2,044","","2,145","","2,346","","2,405"]
["","Unit","","kg","877","","1,062","","1,285","","","1,439","","1,498","","1,559","","1,673","","","1,722","1,842","","1,926","","2,105","","2,229"]
["Water heat exchanger - evaporator","Water flow rate","Nom.","l/s","8.97","","10.29","","11.69","","","14.5","","16.48","","18.51","","20.58","","","22.77","26.29","","29.26","","31.77","","34.57"]
["","Type","","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","","Plate heat exchanger","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger","","Plate heat exchanger"]
["","Water volume","","l","35","","41","","53","","","65","","65","","76","","92","","","92","92","","115","","115","","115"]
["EER","","","","4.494","","4.548","","4.601","","","4.519","","4.468","","4.446","","4.394","","","4.343","4.444","","4.373","","4.311","","4.32"]
["ESEER","","","","5.54","","5.54","","5.52","","","5.54","","5.53","","5.54","","5.52","","","5.51","5.55","","5.51","","5.51","","5.52"]
["Power supply","Phase","","","3~","","3~","","3~","","","3~","","3~","","3~","","3~","","","3~","3~","","3~","","3~","","3~"]
["","Frequency","","Hz","50","","50","","50","","","50","","50","","50","","50","","","50","50","","50","","50","","50"]
["","Voltage","","V","400","","400","","400","","","400","","400","","400","","400","","","400","400","","400","","400","","400"]
["Notes","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation."]
["","","","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation","","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 5/10°C; condensor 40/45°C, unit at full load operation"]
["","","","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","","(3) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding"]
["","","","","(4) - Fluid: Water","","(4) - Fluid: Water","","(4) - Fluid: Water","","","(4) - Fluid: Water","","(4) - Fluid: Water","","(4) - Fluid: Water","","(4) - Fluid: Water","","","(4) - Fluid: Water","(4) - Fluid: Water","","(4) - Fluid: Water","","(4) - Fluid: Water","","(4) - Fluid: Water"]
["","","","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(5) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["","","","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(6) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(7) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current.","","(8) - Max. unit starting current: starting current of biggest compressor + fans current."]
["","","","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","","(9) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current"]
["","","","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope","","(10) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(11) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1","","(12) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["Weight","Unit","","kg","","877","","1062","","1285","1347","","1439","","1498","","1559","","1673","1722","","","1842","","1926","","2105","","2229"]
["","Operation weight","","kg","","957","","1156","","1401","1469","","1575","","1641","","1723","","1851","1918","","","2044","","2145","","2346","","2405"]
["Refrigerant","Charge","","kg","","20","","20","","22","22","","24","","24","","30","","32","34","","","34","","38","","40","","40"]