{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":28,"n_cols":16,"rows_kept":28,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-DZXS"]
[]
[]
[]
[]
["","","","","EWWS320DZXSA1","EWWS440DZXSA1","EWWS530DZXSA1","EWWS610DZXSA2","EWWS640DZXSA2","EWWS700DZXSA1","EWWS880DZXSA2","EWWSC10DZXSA2","EWWSC13DZXSA3","EWWSC14DZXSA2","EWWSC15DZXSA3","EWWSC21DZXSA3"]
["Cooling capacity","Nom.","","kW","316","439","520","609","631","694","876","1,043","1,305","1,390","1,550","2,027"]
["Capacity control","Method","","","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","%","30","21","21","16","15","18","11","11","7","9","8","6"]
["Power input","Cooling","Nom.","kW","67.1","90","103","126","132","127","177","205","270","257","312","384"]
["EER","","","","4.71","4.88","5.05","4.82","4.77","5.44","4.92","5.08","4.82","5.4","4.96","5.27"]
["ESEER","","","","0","0","0","0","0","0","0","0","0","0","0","0"]
["Dimensions","Unit","Depth","mm","3,625","3,625","3,625","3,625","3,585","3,585","3,585","3,580","4,793","3,580","4,768","4,812"]
["","","Height","mm","1,865","1,865","1,865","1,985","1,985","1,985","1,985","2,200","2,083","2,200","2,225","2,290"]
["","","Width","mm","1,055","1,055","1,055","1,160","1,160","1,160","1,160","1,270","1,510","1,270","1,510","1,510"]
["Weight","Unit","","kg","1,700","1,900","2,000","2,850","2,850","2,600","2,900","3,600","4,350","3,800","4,750","5,500"]
["","Operation weight","","kg","1,973","2,216","2,347","3,197","3,344","3,102","3,458","4,292","5,020","4,579","5,540","6,570"]
["Water heat exchanger - evaporator","Type","","","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube"]
["","Water volume","","l","70","96","107","107","134","134","156","199","272","229","317","444"]
["Water heat exchanger - condenser","Type","","","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube","Flooded Shell & Tube"]
["Compressor","Type","","","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor"]
["","Quantity","","","1","1","1","2","2","1","2","2","3","2","3","3"]
["Sound power level","Cooling","Nom.","dBA","87.9","88.9","89.9","91.1","91.0","91.1","92.0","93.3","93.5","94.3","94.8","95.8"]
["Sound pressure level","Cooling","Nom.","dBA","69.6","70.6","71.6","72.6","72.6","72.6","73.6","74.6","73.9","75.6","75.2","76.2"]
["Refrigerant","Type","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","Charge","","kg","120","150","120","140","190","180","200","230","240","230","270","270"]
["","Circuits","Quantity","","1","1","1","1","1","1","1","1","1","1","1","1"]
["","GWP","","","631","631","631","631","631","631","631","631","631","631","631","631"]