{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":74,"n_cols":21,"rows_kept":74,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYD-BZSL"]
[]
[]
[]
[]
["","","","","","EWYD250BZSL","EWYD270BZSL","EWYD290BZSL","EWYD320BZSL","EWYD330BZSL","EWYD360BZSL","EWYD370BZSL","EWYD400BZSL","EWYD430BZSL","EWYD450BZSL","EWYD490BZSL","EWYD510BZSLB3","EWYD510BZSL","EWYD530BZSLB3","EWYD570BZSL","EWYD570BZSLB3"]
["Sound pressure level","Cooling","","Nom.","dBA","76 (4)","76 (4)","76 (4)","76 (4)","76 (4)","76 (4)","76 (4)","76 (4)","76 (4)","77 (4)","77 (4)","77.2","77 (4)","77.2","77 (4)","77.2"]
["Refrigerant charge","Per circuit","","","kg","","","","","","","","","","","47.0","","47.0","","49.0"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","","","","","","","","","","","67.2","","67.2","","70.1"]
["Compressor","Type","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Starting method","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","","Inverter driven","","Inverter driven","","Inverter driven"]
["","Quantity","","","","2","2","2","2","2","2","2","2","2","3","3","3","3","3","3","3"]
["Weight","Operation weight","","","kg","3,888","3,933","3,978","4,343","4,343","4,408","4,478","4,858","4,858","5,765","6,234","6,234","6,474","6,474","6,463","6,463"]
["","Unit","","","kg","3,750","3,795","3,840","4,210","4,210","4,280","4,350","4,730","4,730","5,525","6,005","6,005","6,245","6,245","6,245","6,245"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type"]
["EER","","","","","2.76 (1)","2.66 (1)","2.62 (1)","2.75 (1)","2.68 (1)","2.64 (1)","2.57 (1)","2.66 (1)","2.59 (1)","2.83 (1)","2.77 (1)","2.82","2.73 (1)","2.8","2.61 (1)","2.62"]
["ESEER","","","","","","","","","","","","","","","4.16","","4.10","","3.98"]
["Refrigerant","GWP","","","","","","","","","","","","","","1,430","","1,430","","1,430"]
["","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","Circuits","","Quantity","","","","","","","","","","","","3","","3","","3"]
["","Charge","","","kg","","","","","","","","","","","","141","","141","","147"]
["Cooling capacity","Nom.","","","kW","247 (1)","265 (1)","290 (1)","315 (1)","330 (1)","353 (1)","370 (1)","401 (1)","423 (1)","446 (1)","490 (1)","503","507 (1)","519","565 (1)","569"]
["Water heat exchanger","Water volume","","","l","","","","","","","","","","","229","","229","","218"]
["","Type","","","","","","","","","","","","","","Single pass shell & tube","","Single pass shell & tube","","Single pass shell & tube"]
["Power input","Cooling","","Nom.","kW","","","","","","","","","","","177 (1)","","186 (1)","","216 (1)"]
["","Heating","","Nom.","kW","","","","","","","","","","","178 (2)","","186 (2)","","208 (2)"]
["Sound power level","Cooling","","Nom.","dBA","94","94","94","95","95","95","95","95","95","97","97","97","97","97","97","97"]
["COP","","","","","","","","","","","","","","","2.99 (2)","","3.01 (2)","","2.97 (2)"]
["Dimensions","Unit","","Width","mm","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254","2,254"]
["","","","Depth","mm","3,547","3,547","3,547","4,428","4,428","4,428","4,428","5,329","5,329","6,659","6,659","6,659","6,659","6,659","6,659","6,659"]
["","","","Height","mm","2,335","2,335","2,335","2,335","2,335","2,335","2,335","2,335","2,335","2,280","2,280","2,280","2,280","2,280","2,280","2,280"]
["Capacity control","Minimum capacity","","","%","13.0","13.0","13.0","13.0","13.0","13.0","13.0","13.0","13.0","9.0","9.0","9","9.0","9","9.0","9"]
["","Method","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Variable","Stepless","Variable","Stepless","Variable"]
["Fan","Air flow rate","Cooling","Nom.","l/s","24,432","24,264","24,095","32,576","32,576","32,628","32,127","40,720","40,720","48,863","48,415","","47,732","","48,191"]
["","Speed","","","rpm","","","","","","","","","","","700","","700","","700"]
["Heating capacity","Nom.","","","kW","","","","","","","","","","","533 (2)","","561 (2)","","618 (2)"]
["Compressor","Starting method","","","","","","","","","","","","","","VFD driven","","VFD driven","","VFD driven"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Voltage range","","Max.","%","10","10","10","10","10","10","10","10","10","10","","10","","10","","10"]
["","","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","","-10","","-10","","-10"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["Unit","Max unit current for wires sizing","","","A","238","238","238","287","328","328","328","367","398","370","","451","","492","","492"]
["","Starting current","","Max","A","0","0","0","0","0","0","0","0","0","0","","0","","0","","0"]
["","Running current","Cooling","Nom.","A","147","161","177","187","201","217","230","244","261","258","","291","","305","","305"]
["","","","Max","A","216","216","216","261","298","298","298","334","362","336","","410","","447","","447"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation."]
["","","","","","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation."]
["","","","","","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825."]
["","","","","","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744"]
["","","","","","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","","(11) - Fluid: Water","","(11) - Fluid: Water"]
["","","","","","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["Power input","Cooling","","Nom.","kW","89.5 (1)","99.5 (1)","110 (1)","115 (1)","123 (1)","134 (1)","144 (1)","151 (1)","163 (1)","158 (1)","","178","","185","","217"]
["IPLV","","","","","4.90","4.96","4.91","5.17","5.08","5.12","5.06","5.22","5.13","5.07","","5.03","","4.99","","4.89"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","","Ivory white","","Ivory white","","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet"]
["Fan","Quantity","","","","6","6","6","8","8","8","8","10","10","12","","12","","12","","12"]
["","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","","Direct propeller","","Direct propeller","","Direct propeller"]
["Fan motor","Drive","","","","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","","Direct on line","","Direct on line","","Direct on line"]
["Operation range","Air side","Cooling","Min.","°CDB","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","45","45","45","45","45","45","45","45","45","45"]
["","Water side","Evaporator","Min.","°CDB","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8"]
["","","","Max.","°CDB","15","15","15","15","15","15","15","15","15","15"]
["Refrigerant","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","","1,430.0","","1,430.0","","1,430.0"]
["","Circuits","","Quantity","","2","2","2","2","2","2","2","2","2","3","","3","","3","","3"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","219.1mm","","219.1mm","","219.1mm","","219.1mm"]
["SEER","","","","","","","","","","","","","","","","4.56","","4.6","","4.55"]