{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":6,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-DF"]
[]
[]
[]
[]
["","","","","","FWC07DAFN5V3--"]
["Cooling capacity (standard conditions)","Sensible capacity 4-pipe","","Low","kW","3.26"]
["","","","High","kW","5.58"]
["","Total capacity 4-pipe","","Low","kW","4.35"]
["","","","High","kW","7.15"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","5.34"]
["","","","High","kW","8.82"]
["Power input","Low","","","kW","0.02"]
["","High","","","kW","0.069"]
["Dimensions","Unit","","Height","mm","287"]
["","","","Width","mm","837"]
["","","","Depth","mm","921"]
["Weight","Unit","","","kg","27"]
["Fan","Air flow rate","","Low","m³/h","686"]
["","","","High","m³/h","1296"]
["Total sound power level","Low","","","dBA","36"]
["","High","","","dBA","52"]
["Sound pressure level","Low","","","dBA","23"]
["","High","","","dBA","39"]
["Water flow","Cooling","","Low","l/h","776"]
["","","","High","l/h","1295"]
["","Heating","","Low","l/h","459"]
["","","","High","l/h","759"]
["","Water pressure drop","Cooling","Low","kPa","13"]
["","","","High","kPa","25"]
["","","Heating","Low","kPa","13"]
["","","","High","kPa","24"]
["Piping connections","Water","","Inlet","","3/4\" BSP (female thread)"]
["","","","Outlet","","3/4\" BSP (female thread)"]
["","Drain","","OD","mm","VP25 (External dia.32; internal dia. 25)"]
["Power supply","Type","","","","230 / 1 / 50"]
["","Phase","","","","1~"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","230"]
["Notes","","","","","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C"]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C"]
["","","","","","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C"]
["","","","","","(4) - Do not let water of less than 5°C or more than 90°C enter the unit, this may damage the unit .."]
["","","","","","(5) - Airflow: 20°C DB, 15°C WB; 230V 50Hz 0Pa .."]