{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":9,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-DT"]
[]
[]
[]
[]
["","","","","","FWC06DATN5V3--","FWC07DATN5V3--","FWC08DATN5V3--","FWC09DATN5V3--"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","3.04","3.38","3.63","3.69"]
["","","","High","kW","4.9","5.87","6.87","7.84"]
["","Total capacity 2-pipe","","Low","kW","4.06","4.51","4.81","4.88"]
["","","","High","kW","6.34","7.53","8.7","9.66"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","Low","kW","4.15","4.62","4.94","5.02"]
["","","","High","kW","6.79","8.14","9.51","10.7"]
["Power input","Low","","","kW","0.02","0.02","0.03","0.03"]
["","High","","","kW","0.045","0.071","0.104","0.167"]
["Dimensions","Unit","","Height","mm","287","287","287","287"]
["","","","Width","mm","837","837","837","837"]
["","","","Depth","mm","921","921","921","921"]
["Weight","Unit","","","kg","25","25","25","25"]
["Fan","Air flow rate","","Low","m³/h","621","697","747","757"]
["","","","High","m³/h","1080","1336","1615","1881"]
["Total sound power level","Low","","","dBA","35","35","36","39"]
["","High","","","dBA","46","52","56","61"]
["Sound pressure level","Low","","","dBA","22","22","23","26"]
["","High","","","dBA","33","39","43","48"]
["Water flow","Cooling","","Low","l/h","698","776","827","839"]
["","","","High","l/h","1090","1295","1496","1661"]
["","Heating","","Low","l/h","713","794","850","863"]
["","","","High","l/h","1167","1400","1635","1841"]
["","Water pressure drop","Cooling","Low","kPa","12","14","15","16"]
["","","","High","kPa","20","27","33","40"]
["","","Heating","Low","kPa","11","13","14","15"]
["","","","High","kPa","20","27","36","44"]
["Piping connections","Water","","Inlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["","","","Outlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["","Drain","","OD","mm","VP25 (External dia.32; internal dia. 25)","VP25 (External dia.32; internal dia. 25)","VP25 (External dia.32; internal dia. 25)","VP25 (External dia.32; internal dia. 25)"]
["Power supply","Type","","","","230 / 1 / 50","230 / 1 / 50","230 / 1 / 50","230 / 1 / 50"]
["","Phase","","","","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","230","230","230","230"]
["Notes","","","","","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C"]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C"]
["","","","","","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C"]
["","","","","","(4) - Do not let water of less than 5°C or more than 90°C enter the unit, this may damage the unit ..","(4) - Do not let water of less than 5°C or more than 90°C enter the unit, this may damage the unit ..","(4) - Do not let water of less than 5°C or more than 90°C enter the unit, this may damage the unit ..","(4) - Do not let water of less than 5°C or more than 90°C enter the unit, this may damage the unit .."]
["","","","","","(5) - Airflow: 20°C DB, 15°C WB; 230V 50Hz 0Pa ..","(5) - Airflow: 20°C DB, 15°C WB; 230V 50Hz 0Pa ..","(5) - Airflow: 20°C DB, 15°C WB; 230V 50Hz 0Pa ..","(5) - Airflow: 20°C DB, 15°C WB; 230V 50Hz 0Pa .."]