{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":9,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWI-AF"]
[]
[]
[]
[]
["","","","","","FWI02AAFN6V3","FWI04AAFN6V3","FWI06AAFN6V3","FWI08AAFN6V3"]
["Cooling capacity (standard conditions)","Sensible capacity 4-pipe","","Low","kW","1.46 (1)","2.10 (1)","3.34 (1)","4.50 (1)"]
["","","","High","kW","2.23 (1)","3.58 (1)","5.03 (1)","7.56 (1)"]
["","Total capacity 4-pipe","","Low","kW","1.85 (1)","2.62 (1)","4.61 (1)","6.09 (1)"]
["","","","High","kW","2.60 (1)","4.41 (1)","6.61 (1)","9.50 (1)"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","2.90 (3)","3.73 (3)","7.01 (3)","8.96 (3)"]
["","","","High","kW","3.86 (3)","5.51 (3)","9.53 (3)","12.90 (3)"]
["Power input","Low","","","kW","0.007","0.009","0.014","0.025"]
["","High","","","kW","0.018","0.067","0.036","0.150"]
["Dimensions","Unit","","Height","mm","298","298","350","350"]
["","","","Width","mm","577","577","793","793"]
["","","","Depth","mm","577","577","793","793"]
["Weight","Unit","","","kg","23.0","23.0","43.0","43.0"]
["Decoration panel","Dimensions","Unit","Height","mm","41","41","75","75"]
["","","","Width","mm","730","730","860","860"]
["","","","Depth","mm","730","730","860","860"]
["Fan","Air flow rate","","Low","m³/h","356","395","687","956"]
["","","","High","m³/h","610","982","1,137","1,823"]
["Total sound power level","Low","","","dBA","35.0 (4)","38.0 (4)","35.0 (4)","43.0 (4)"]
["","High","","","dBA","46.0 (4)","61.0 (4)","45.0 (4)","58.0 (4)"]
["Sound pressure level","Low","","","dBA","35.0 (4)","38.0 (4)","35.0 (4)","43.0 (4)"]
["","High","","","dBA","46.0 (4)","61.0 (4)","45.0 (4)","58.0 (4)"]
["Water flow","Cooling","","Low","l/h","317 (1)","451 (1)","792 (1)","1,045 (1)"]
["","","","High","l/h","447 (1)","759 (1)","1,135 (1)","1,631 (1)"]
["","Heating","","High","l/h","338 (3)","474 (3)","834 (3)","1,133 (3)"]
["","","","Low","l/h","254 (3)","321 (3)","613 (3)","785 (3)"]
["","Water pressure drop","Cooling","Low","kPa","4 (1)","7 (1)","12 (1)","17 (1)"]
["","","","High","kPa","8 (1)","25 (1)","22 (1)","37 (1)"]
["","","Heating","Low","kPa","6 (3)","4 (3)","11 (3)","18 (3)"]
["","","","High","kPa","11 (3)","11 (3)","19 (3)","33 (3)"]
["Allowed water temperature","Cooling","","Min.","°C","5","5","5","5"]
["","Heating","","Max.","°C","80","80","80","80"]
["Piping connections","Water","","Inlet","","1/2\"","1/2\"","3/4\"","3/4\""]
["","","","Outlet","","1/2\"","1/2\"","3/4\"","3/4\""]
["","Drain","","OD","mm","10","10","10","10"]
["Water connections","Primary coil","","","inch","1/2\"","1/2\"","3/4\"","3/4\""]
["","Additional coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\""]
["Control systems","Wired remote control","","","","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit."]