{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":11,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXT-ATV3CL"]
[]
[]
[]
[]
["","","","","","FWXT10AATV3CL","FWXT10ABTV3CL","FWXT15AATV3CL","FWXT15ABTV3CL","FWXT20AATV3CL","FWXT20ABTV3CL"]
["Dimensions","Unit","","Width","mm","902","","1,100","","1,300"]
["","","","Depth","mm","128","","128","","128"]
["","","","Height","mm","335","","335","","335"]
["Casing","Colour","","","","RAL 9003","","RAL 9003","","RAL 9003"]
["Weight","Unit","","","kg","14.0","","16.0","","19.0"]
["Power supply","Phase","","","","1~","","1~","","1~"]
["","Frequency","","","Hz","50","","50","","50"]
["","Voltage","","","V","230","","230","","230"]
["Cooling capacity","7/12°C","","Min.","kW","","0.49","","0.62","","0.70"]
["","","","Med.","kW","","0.88","","1.08","","1.21"]
["","","","Max.","kW","","1.24","","1.61","","1.94"]
["Sensible cooling capacity","7/12°C","","Min.","kW","","0.37","","0.52","","0.57"]
["","","","Med.","kW","","0.70","","0.86","","1.02"]
["","","","Max.","kW","","0.98","","1.27","","1.52"]
["Heating capacity","45/40°C","","Min.","kW","","0.55","","0.79","","0.74"]
["","","","Med.","kW","","1.00","","1.36","","1.55"]
["","","","Max.","kW","","1.50","","2.01","","2.13"]
["Power input","Min.","","","kW","","0.01","","0.01","","0.01"]
["","Med.","","","kW","","0.01","","0.01","","0.01"]
["","Max.","","","kW","","0.02","","0.02","","0.03"]
["Fan speed","Min.","","","rpm","","680.00","","680.00","","680.00"]
["","Med.","","","rpm","","1100.00","","1100.00","","1100.00"]
["","Max.","","","rpm","","1500.00","","1500.00","","1500.00"]
["Casing","Colour","","","","","RAL 9003","","RAL 9003","","RAL 9003"]
["","Material","","","","","Sheet metal","","Sheet metal","","Sheet metal"]
["Dimensions","Unit","","Height","mm","","335","","335","","335"]
["","","","Width","mm","","902","","1102","","1302"]
["","","","Depth","mm","","128","","128","","128"]
["","Packed unit","","Height","mm","","490","","490","","490"]
["","","","Width","mm","","1030","","1230","","1430"]
["","","","Depth","mm","","210","","210","","210"]
["Weight","Unit","","","kg","","14","","16","","19"]
["","Packed unit","","","kg","","15","","17","","20"]
["Packing","Material","","","","","Carton","","Carton","","Carton"]
["","Weight","","","kg","","1","","1","","1"]
["Heat exchanger","Quantity","","","","","1","","1","","1"]
["","Internal coil volume","","","l","","0.5","","0.61","","0.77"]
["","Charging","","Operating pressure","bar","","10","","10","","10"]
["Water circuit","Piping connections diameter","","","in","","3/4","","3/4","","3/4"]
["","Piping material","","","","","COPPER","","COPPER","","COPPER"]
["","Pressure","Heating","Max.","bar","","10","","10","","10"]
["Water circuit - water pressure drop","Heating","45/40°C","Min.","kPa","","5.10","","4.81","","6.00"]
["","","","Med.","kPa","","12.00","","6.30","","6.40"]
["","","","Max.","kPa","","16.30","","7.20","","8.10"]
["","Cooling","7/12°C","Min.","kPa","","4.80","","4.70","","5.50"]
["","","","Med.","kPa","","10.50","","5.60","","5.40"]
["","","","Max.","kPa","","11.70","","5.10","","5.30"]
["Water circuit - water flow rate","Heating","45/40°C","Min.","kg/h","","100.00","","140","","150.00"]
["","","","Med.","kg/h","","170.00","","240","","300.00"]
["","","","Max.","kg/h","","260.00","","350","","420.00"]
["","Cooling","7/12°C","Min.","kg/h","","80.00","","110","","120.00"]
["","","","Med.","kg/h","","150.00","","190","","210.00"]
["","","","Max.","kg/h","","210.00","","280","","330.00"]
["Sound power level","Min.","","","dBA","","35","","36","","37"]
["","Med.","","","dBA","","46","","47","","48"]
["","Max.","","","dBA","","53.0","","54.0","","55.0"]
["Operation range","Heating","Water side","Min.","°C","","30","","30","","30"]
["","","","Max.","°C","","85","","85","","85"]
["","Cooling","Water side","Min.","°C","","5","","5","","5"]
["","","","Max.","°C","","18","","18","","18"]
["","Indoor installation","Ambient","Min.","°CDB","","0","","0","","0"]
["","","","Max.","°CDB","","45","","45","","45"]
["Control systems","Infrared remote control","","","","","For FWXT-ATV3(C)(CL)","","For FWXT-ATV3(C)(CL)","","For FWXT-ATV3(C)(CL)"]
["","Integrated on indoor unit","","","","","Yes","","Yes","","Yes"]
["Power supply","Phase","","","","","1~","","1~","","1~"]
["","Frequency","","","Hz","","50","","50","","50"]
["","Voltage","","","V","","230","","230","","230"]
["Electrical power consumption","Max.","","","W","","19","","20","","29"]
["","Standby","","","W","","3","","4","","5"]
["Current","Maximum running current","","Heating","A","","0.16","","0.18","","0.24"]
["","","","Cooling","A","","0.16","","0.18","","0.24"]