{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":11,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXV-ATV3R"]
[]
[]
[]
[]
["","","","","","FWXV10AATV3R","FWXV10ABTV3R","FWXV15AATV3R","FWXV15ABTV3R","FWXV20AATV3R","FWXV20ABTV3R"]
["Dimensions","Unit","","Width","mm","999","","1,200","","1,400"]
["","","","Depth","mm","135","","135","","135"]
["","","","Height","mm","601","","601","","601"]
["Casing","Colour","","","","RAL 9003","","RAL 9003","","RAL 9003"]
["Weight","Unit","","","kg","20.0","","23.0","","26.0"]
["Power supply","Phase","","","","1~","","1~","","1~"]
["","Frequency","","","Hz","50","","50","","50"]
["","Voltage","","","V","230","","230","","230"]
["Cooling capacity","7/12°C","","Min.","kW","","0.78","","1.10","","1.13"]
["","","","Med.","kW","","1.11","","1.65","","1.98"]
["","","","Max.","kW","","1.62","","2.64","","2.99"]
["Sensible cooling capacity","7/12°C","","Min.","kW","","0.58","","0.82","","0.85"]
["","","","Med.","kW","","0.71","","1.15","","1.55"]
["","","","Max.","kW","","1.25","","1.91","","2.33"]
["Heating capacity","45/40°C","","Min.","kW","","0.87","","1.12","","1.11"]
["","","","Med.","kW","","1.27","","1.83","","2.32"]
["","","","Max.","kW","","1.96","","2.86","","3.50"]
["Power input","Min.","","","kW","","0.01","","0.01","","0.01"]
["","Med.","","","kW","","0.01","","0.01","","0.01"]
["","Max.","","","kW","","0.02","","0.03","","0.03"]
["Fan speed","Min.","","","rpm","","720.00","","720.00","","720.00"]
["","Med.","","","rpm","","1220.00","","1220.00","","1220.00"]
["","Max.","","","rpm","","1700.00","","1700.00","","1700.00"]
["Casing","Colour","","","","","RAL 9003","","RAL 9003","","RAL 9003"]
["","Material","","","","","Sheet metal","","Sheet metal","","Sheet metal"]
["Dimensions","Unit","","Height","mm","","601","","601","","601"]
["","","","Width","mm","","999","","1199","","1399"]
["","","","Depth","mm","","135","","135","","135"]
["","Packed unit","","Height","mm","","690","","690","","690"]
["","","","Width","mm","","1230","","1430","","1630"]
["","","","Depth","mm","","210","","210","","210"]
["Weight","Unit","","","kg","","20","","23","","26"]
["","Packed unit","","","kg","","21","","24","","27"]
["Packing","Material","","","","","Carton","","Carton","","Carton"]
["","Weight","","","kg","","1","","1","","1"]
["Heat exchanger","Quantity","","","","","1","","1","","1"]
["","Internal coil volume","","","l","","0.8","","1.1","","1.5"]
["","Charging","","Operating pressure","bar","","10","","10","","10"]
["Water circuit","Piping connections diameter","","","in","","3/4","","3/4","","3/4"]
["","Piping material","","","","","COPPER","","COPPER","","COPPER"]
["","Pressure","Heating","Max.","bar","","10","","10","","10"]
["Water circuit - water pressure drop","Heating","45/40°C","Min.","kPa","","7.00","","9.00","","8.00"]
["","","","Med.","kPa","","8.00","","14.00","","15.00"]
["","","","Max.","kPa","","11.00","","23.00","","22.00"]
["","Cooling","7/12°C","Min.","kPa","","7.00","","9.00","","8.00"]
["","","","Med.","kPa","","8.00","","14.00","","15.00"]
["","","","Max.","kPa","","11.00","","23.00","","22.00"]
["Water circuit - water flow rate","Heating","45/40°C","Min.","kg/h","","150.00","","200.00","","190.00"]
["","","","Med.","kg/h","","220.00","","320.00","","400.00"]
["","","","Max.","kg/h","","340.00","","500.00","","610.00"]
["","Cooling","7/12°C","Min.","kg/h","","130.00","","190.00","","190.00"]
["","","","Med.","kg/h","","190.00","","280.00","","340.00"]
["","","","Max.","kg/h","","280.00","","450.00","","510.00"]
["Sound power level","Min.","","","dBA","","40","","42","","43"]
["","Med.","","","dBA","","47","","49","","50"]
["","Max.","","","dBA","","56.0","","57.0","","58.0"]
["Operation range","Heating","Water side","Min.","°C","","30","","30","","30"]
["","","","Max.","°C","","85","","85","","85"]
["","Cooling","Water side","Min.","°C","","5","","5","","5"]
["","","","Max.","°C","","18","","18","","18"]
["","Indoor installation","Ambient","Min.","°CDB","","0","","0","","0"]
["","","","Max.","°CDB","","45","","45","","45"]
["Control systems","Infrared remote control","","","","","No","","No","","No"]
["","Integrated on indoor unit","","","","","Yes","","Yes","","Yes"]
["Power supply","Phase","","","","","1~","","1~","","1~"]
["","Frequency","","","Hz","","50","","50","","50"]
["","Voltage","","","V","","230","","230","","230"]
["Electrical power consumption","Max.","","","W","","19","","25","","31"]
["","Standby","","","W","","3","","4","","5"]
["Current","Maximum running current","","Heating","A","","0.15","","0.21","","0.27"]
["","","","Cooling","A","","0.15","","0.21","","0.27"]