{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":55,"n_cols":12,"rows_kept":55,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXAQ-A"]
[]
[]
[]
[]
["","","","","","FXAQ15AUV1B","FXAQ20AUV1B","FXAQ25AUV1B","FXAQ32AUV1B","FXAQ40AUV1B","FXAQ50AUV1B","FXAQ63AUV1B"]
["Sound pressure level","Heating","","At high fan speed","dBA","33.0","34.0","36.0","38.5","38.0","42.0","47.0"]
["","","","At low fan speed","dBA","28.5","28.5","28.5","28.5","33.5","35.5","38.5"]
["","Cooling","","At low fan speed","dBA","28.5","28.5","28.5","28.5","33.5","35.5","38.5"]
["","","","At high fan speed","dBA","32.0","33.0","35.0","37.5","37.0","41.0","46.5"]
["Standard Accessories","Installation and operation manual","","","","1","1","1","1","1","1","1"]
["","Installation panel","","","","1","1","1","1","1","1","1"]
["","Paper pattern for installation","","","","1","1","1","1","1","1","1"]
["","Insulation tape","","","","1","1","1","1","1","1","1"]
["","Clamps","","","","1","1","1","1","1","1","1"]
["","Screws","","","","1","1","1","1","1","1","1"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.02","0.02","0.03","0.03","0.02","0.03","0.05"]
["","Heating","","At high fan speed","kW","0.03","0.03","0.03","0.04","0.02","0.04","0.06"]
["Cooling capacity","Total capacity","","At high fan speed","kW","1.7 (1)","2.2 (1)","2.8 (1)","3.6 (1)","4.5 (1)","5.6 (1)","7.1 (1)"]
["Piping connections","Liquid","","OD","mm","6.35","6.35","6.35","6.35","6.35","6.35","9.52"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","12.7","12.7","12.7","12.7","12.7","12.7","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","VP13 (I.D. 15/O.D. 18)","VP13 (I.D. 15/O.D. 18)","VP13 (I.D. 15/O.D. 18)","VP13 (I.D. 15/O.D. 18)","VP13 (I.D. 15/O.D. 18)","VP13 (I.D. 15/O.D. 18)","VP13 (I.D. 15/O.D. 18)"]
["Sound power level","Cooling","","At high fan speed","dBA","51.0","52.0","53.0","55.0","55.0","58.0","63.0"]
["Air filter","Type","","","","Washable resin net","Washable resin net","Washable resin net","Washable resin net","Washable resin net","Washable resin net","Washable resin net"]
["Dimensions","Unit","","Width","mm","795","795","795","795","1,050","1,050","1,050"]
["","","","Depth","mm","266","266","266","266","269","269","269"]
["","","","Height","mm","290","290","290","290","290","290","290"]
["Casing","Colour","","","","White","White","White","White","White","White","White"]
["Weight","Unit","","","kg","12","12","12","12","15","15","15"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","8.4","9.1","9.4","9.8","12.2","14.4","18.3"]
["","","","At low fan speed","m³/min","7.0","7.0","7.0","7.0","9.7","11.5","13.5"]
["Heating capacity","Total capacity","","At high fan speed","kW","1.9 (2)","2.5 (2)","3.2 (2)","4.0 (2)","5.0 (2)","6.3 (2)","8.0 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","16","16","16","16","16","16"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~","1~"]
["","Name","","","","V1","V1","V1","V1","V1","V1","V1"]
["","Frequency","","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m (horizontal)"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m (horizontal)"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - Sound levels are measured in an anechoic room.","(4) - Sound levels are measured in an anechoic room.","(4) - Sound levels are measured in an anechoic room.","(4) - Sound levels are measured in an anechoic room.","(4) - Sound levels are measured in an anechoic room.","(4) - Sound levels are measured in an anechoic room.","(4) - Sound levels are measured in an anechoic room."]
["","","","","","(5) - Operation sound differs with operation and ambient conditions","(5) - Operation sound differs with operation and ambient conditions","(5) - Operation sound differs with operation and ambient conditions","(5) - Operation sound differs with operation and ambient conditions","(5) - Operation sound differs with operation and ambient conditions","(5) - Operation sound differs with operation and ambient conditions","(5) - Operation sound differs with operation and ambient conditions"]
["","","","","","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(9) - MCA/MFA: MCA = 1.25 x FLA","(9) - MCA/MFA: MCA = 1.25 x FLA","(9) - MCA/MFA: MCA = 1.25 x FLA","(9) - MCA/MFA: MCA = 1.25 x FLA","(9) - MCA/MFA: MCA = 1.25 x FLA","(9) - MCA/MFA: MCA = 1.25 x FLA","(9) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases"]
["","","","","","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker"]
["","","","","","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA"]
["","","","","","(13) - Next lower standard fuse rating minimum 16A","(13) - Next lower standard fuse rating minimum 16A","(13) - Next lower standard fuse rating minimum 16A","(13) - Next lower standard fuse rating minimum 16A","(13) - Next lower standard fuse rating minimum 16A","(13) - Next lower standard fuse rating minimum 16A","(13) - Next lower standard fuse rating minimum 16A"]
["","","","","","(14) - MFA ≤ 4 x FLA","(14) - MFA ≤ 4 x FLA","(14) - MFA ≤ 4 x FLA","(14) - MFA ≤ 4 x FLA","(14) - MFA ≤ 4 x FLA","(14) - MFA ≤ 4 x FLA","(14) - MFA ≤ 4 x FLA"]