{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":236,"n_cols":21,"rows_kept":236,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","REYA-A"]
[]
[]
[]
[]
["","","","","","REYA8A7Y1B","REYA10A7Y1B.","REYA10A7Y1B","REYA12A7Y1B","REYA13A7Y1B","REYA14A7Y1B","REYA16A7Y1B.","REYA16A7Y1B","REYA18A7Y1B.","REYA18A7Y1B","REYA20A7Y1B","REYA20A7Y1B.","REYA22A7Y1B","REYA24A7Y1B","REYA26A7Y1B","REYA28A7Y1B"]
["System","Outdoor unit module 1","","","","","","","","REMA5A","","REYA8A","","REYA8A","","","","REYA10A","REYA8A","REYA12A","REYA12A"]
["","Outdoor unit module 2","","","","","","","","REYA8A","","REYA8A","","REYA10A","","","","REYA12A","REYA16A","REYA14A","REYA16A"]
["Recommended combination","","","","","4 x FXFA50A2VEB","4 x FXFA63A2VEB","4 x FXFA63A2VEB","6 x FXFA50A2VEB","3 x FXFA50A2VEB + 3 x FXFA63A2VEB","1 x FXFA50A2VEB + 5 x FXFA63A2VEB","4 x FXFA63A2VEB + 2 x FXFA80A2VEB","4 x FXFA63A2VEB + 2 x FXFA80A2VEB","4 x FXFA50A2VEB + 4 x FXFA63A2VEB","3 x FXFA50A2VEB + 5 x FXFA63A2VEB","8 x FXFA63A2VEB","10 x FXFA50A2VEB","6 x FXFA50A2VEB + 4 x FXFA63A2VEB","4 x FXFA50A2VEB + 4 x FXFA63A2VEB + 2 x FXFA80A2VEB","7 x FXFA50A2VEB + 5 x FXFA63A2VEB","6 x FXFA50A2VEB + 4 x FXFA63A2VEB + 2 x FXFA80A2VEB"]
["Recommended combination 2","","","","","4 x FXSA50A2VEB","4 x FXSA63A2VEB","4 x FXSA63A2VEB","6 x FXSA50A2VEB","3 x FXSA50A2VEB + 3 x FXSA63A2VEB","1 x FXSA50A2VEB + 5 x FXSA63A2VEB","4 x FXSA63A2VEB + 2 x FXSA80A2VEB","4 x FXSA63A2VEB + 2 x FXSA80A2VEB","4 x FXSA50A2VEB + 4 x FXSA63A2VEB","3 x FXSA50A2VEB + 5 x FXSA63A2VEB","8 x FXSA63A2VEB","10 x FXSA50A2VEB","6 x FXSA50A2VEB + 4 x FXSA63A2VEB","4 x FXSA50A2VEB + 4 x FXSA63A2VEB + 2 x FXSA80A2VEB","7 x FXSA50A2VEB + 5 x FXSA63A2VEB","6 x FXSA50A2VEB + 4 x FXSA63A2VEB + 2 x FXSA80A2VEB"]
["Recommended combination 3","","","","","4 x FXMA50A5VEB","4 x FXMA63A5VEB","4 x FXMA63A5VEB","6 x FXMA50A5VEB","3 x FXMA50A5VEB + 3 x FXMA50A5VEB","1 x FXMA50A5VEB + 5 x FXMA63A5VEB","4 x FXMA63A5VEB + 2 x FXMA80A5VEB","4 x FXMA63A5VEB + 2 x FXMA80A5VEB","4 x FXMA50A5VEB + 4 x FXMA63A5VEB","3 x FXMA50A5VEB + 5 x FXMA63A5VEB","8 x FXMA63A5VEB","10 x FXMA50A5VEB","6 x FXMA50A5VEB + 4 x FXMA63A5VEB","4 x FXMA50A5VEB + 4 x FXMA63A5VEB + 2 x FXMA80A5VEB","7 x FXMA50A5VEB + 5 x FXMA63A5VEB","6 x FXMA50A5VEB + 4 x FXMA63A5VEB + 2 x FXMA80A5VEB"]
["Continuous heating","","","","","","Yes","","","Yes","","Yes","","Yes","","","Yes","Yes","Yes","Yes","Yes"]
["Heating capacity","Nom.","","6°CWB","kW","22.4 (2)","","","33.5 (2)","36.4 (2)","40.0 (2)","44.8 (2)","45.0 (2)","50.4 (2)","50.4 (2)","","","61.5 (2)","67.4 (2)","73.5 (2)","78.5 (2)"]
["COP at nom. capacity","6°CWB","","","kW/kW","3.83 (2)","","","3.46 (2)","3.76 (2)","3.57 (2)","3.72 (2)","3.52 (2)","3.61 (2)","3.66 (2)","","","3.46 (2)","3.62 (2)","3.52 (2)","3.49 (2)"]
["SCOP","","","","","4.11","4.09","4.33","4.49","4.11","4.28","4.35","4.26","4.34","4.39","4.14","4.38","4.41","4.20","4.38","4.36"]
["SCOP recommended combination 2","","","","","4.10","4.14","4.34","4.56","4.19","4.33","4.38","4.33","4.40","4.33","4.11","4.48","4.45","4.24","4.44","4.43"]
["SCOP recommended combination 3","","","","","4.15","4.16","4.40","4.56","4.22","4.33","4.37","4.32","4.46","4.39","4.14","4.50","4.48","4.25","4.44","4.43"]
["SEER","","","","","7.35","7.62","7.14","7.21","7.49","7.73","7.40","7.10","7.26","7.09","6.63","7.27","7.17","7.16","7.48","7.15"]
["SEER recommended combination 2","","","","","7.07","7.3","6.87","6.90","7.15","7.53","6.93","7.01","6.95","6.94","6.57","6.94","6.88","7.01","7.23","6.96"]
["SEER recommended combination 3","","","","","7.49","7.61","7.15","7.41","7.57","7.78","7.31","7.15","7.30","7.11","6.64","7.48","7.28","7.29","7.61","7.26"]
["Space cooling","A Condition (35°C - 27/19)","","EERd","","3.25","","","3.24","3.46","3.26","3.25","3.23","3.26","2.73","","","3.25","3.24","3.25","3.23"]
["","","","Pdc","kW","22.4","","","33.5","36.4","40.0","44.8","45.0","50.4","50.4","","","61.5","67.4","73.5","78.5"]
["","B Condition (30°C - 27/19)","","EERd","","5.23","","","4.60","6.08","4.92","5.41","4.58","5.18","4.47","","","4.78","4.78","4.77","4.59"]
["","","","Pdc","kW","16.5","","","24.7","26.8","29.5","33.0","33.2","37.1","37.1","","","45.3","49.7","54.2","57.8"]
["","C Condition (25°C - 27/19)","","EERd","","9.11","","","8.45","9.04","8.74","9.11","8.25","8.76","8.15","","","8.47","8.52","8.61","8.33"]
["","","","Pdc","kW","10.6","","","15.9","18.0","18.9","21.2","21.3","23.9","23.9","","","29.1","31.9","34.8","37.2"]
["","D Condition (20°C - 27/19)","","EERd","","15.3","","","17.7","13.9","22.5","15.0","16.7","15.0","20.7","","","16.2","16.0","20.1","17.1"]
["","","","Pdc","kW","8.13","","","8.57","15.5","10.9","15.9","11.1","16.3","12.0","","","16.8","19.2","19.5","19.7"]
["Space cooling recommended combination 2","A Condition (35°C - 27/19)","","EERd","","3.23","","","3.00","3.36","3.23","3.14","3.06","3.23","2.64","","","3.10","3.11","3.12","3.03"]
["","","","Pdc","kW","22.4","","","33.5","36.4","40.0","44.8","45.0","50.4","50.4","","","61.5","67.4","73.5","78.5"]
["","B Condition (30°C - 27/19)","","EERd","","5.09","","","4.54","5.78","4.85","5.00","4.64","4.94","4.43","","","4.67","4.78","4.71","4.60"]
["","","","Pdc","kW","16.5","","","24.7","26.8","29.5","33.0","33.2","37.1","37.1","","","45.3","49.7","54.2","57.8"]
["","C Condition (25°C - 27/19)","","EERd","","8.55","","","7.94","8.53","8.38","8.36","8.11","8.27","7.87","","","8.00","8.25","8.17","8.04"]
["","","","Pdc","kW","10.6","","","15.9","17.8","18.9","21.2","21.3","23.9","23.9","","","29.1","31.9","34.8","37.2"]
["","D Condition (20°C - 27/19)","","EERd","","14.6","","","16.9","13.3","21.7","14.3","16.5","14.3","20.0","","","15.4","15.6","19.3","16.7"]
["","","","Pdc","kW","7.84","","","8.20","15.0","10.6","15.5","10.8","15.8","11.6","","","16.2","18.6","18.8","19.0"]
["Space cooling recommended combination 3","A Condition (35°C - 27/19)","","EERd","","3.22","","","3.23","3.41","3.30","3.18","3.04","3.25","2.66","","","3.25","3.13","3.27","3.12"]
["","","","Pdc","kW","22.4","","","33.5","36.4","40.0","44.8","45.0","50.4","50.4","","","61.5","67.4","73.5","78.5"]
["","B Condition (30°C - 27/19)","","EERd","","5.31","","","4.69","6.12","4.93","5.24","4.64","5.08","4.49","","","4.79","4.94","4.82","4.66"]
["","","","Pdc","kW","16.5","","","24.7","26.8","29.5","33.0","33.2","37.1","37.1","","","45.3","49.7","54.1","57.8"]
["","C Condition (25°C - 27/19)","","EERd","","9.41","","","8.82","9.22","8.84","9.04","8.50","8.94","8.22","","","8.71","8.77","8.83","8.64"]
["","","","Pdc","kW","10.6","","","15.9","18.1","18.9","21.2","21.3","23.9","23.9","","","29.1","31.9","34.8","37.2"]
["","D Condition (20°C - 27/19)","","EERd","","15.7","","","18.5","14.2","22.4","15.2","16.7","15.4","20.9","","","16.6","16.2","20.5","17.5"]
["","","","Pdc","kW","8.19","","","8.50","15.5","10.9","16.0","10.7","16.3","11.9","","","16.6","18.9","19.4","19.3"]
["Space heating (Average climate)","TBivalent","","COPd (declared COP)","","2.80","","","2.38","2.74","2.57","2.87","2.53","2.51","2.36","","","2.33","2.62","2.48","2.46"]
["","","","Pdh (declared heating cap)","kW","13.7","","","18.4","21.7","20.6","23.2","23.2","27.9","27.9","","","34.4","36.9","39.0","41.6"]
["","","","Tbiv (bivalent temperature)","°C","-10","","","-10","-10","-10","-10","-10","-10","-10","","","-10","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","2.80","","","2.38","2.74","2.57","2.87","2.53","2.51","2.36","","","2.33","2.62","2.48","2.46"]
["","","","Pdh (declared heating cap)","kW","13.7","","","18.4","21.7","20.6","23.2","23.2","27.9","27.9","","","34.4","36.9","39.0","41.6"]
["","","","Tol (temperature operating limit)","°C","-10","","","-10","-10","-10","-10","-10","-10","-10","","","-10","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","3.06","","","2.84","3.03","2.94","3.18","2.87","2.87","2.70","","","2.76","2.94","2.89","2.85"]
["","","","Pdh (declared heating cap)","kW","12.1","","","16.3","19.2","18.2","20.5","20.5","24.7","24.7","","","30.4","32.6","34.5","36.8"]
["","B Condition (2°C)","","COPd (declared COP)","","3.81","","","4.15","4.02","3.86","4.17","3.93","4.20","4.19","","","4.19","3.89","3.99","4.03"]
["","","","Pdh (declared heating cap)","kW","7.38","","","9.89","11.7","11.1","12.5","12.5","15.0","15.0","","","18.5","19.9","21.0","22.4"]
["","C Condition (7°C)","","COPd (declared COP)","","5.27","","","6.32","5.11","6.31","5.45","6.21","5.60","6.22","","","6.02","5.82","6.32","6.26"]
["","","","Pdh (declared heating cap)","kW","4.76","","","6.36","8.40","7.13","8.05","8.03","9.66","9.66","","","11.9","12.8","13.5","14.4"]
["","D Condition (12°C)","","COPd (declared COP)","","7.04","","","9.14","6.47","6.68","6.93","6.04","7.49","6.85","","","8.49","6.47","7.76","7.33"]
["","","","Pdh (declared heating cap)","kW","4.51","","","5.52","8.93","5.15","9.04","5.07","9.97","6.24","","","11.0","9.58","10.7","10.6"]
["Space heating (Average climate) recommended combination 2","A Condition (-7°C)","","COPd (declared COP)","","3.00","","","2.83","3.05","2.95","3.18","2.89","2.86","2.62","","","2.73","2.93","2.89","2.86"]
["","","","Pdh (declared heating cap)","kW","12.1","","","16.3","19.2","18.2","20.5","20.5","24.7","24.7","","","30.4","32.6","34.5","36.8"]
["","B Condition (2°C)","","COPd (declared COP)","","3.80","","","4.26","4.12","3.89","4.18","3.96","4.27","4.07","","","4.25","3.90","4.06","4.09"]
["","","","Pdh (declared heating cap)","kW","7.45","","","9.89","11.7","11.1","12.5","12.5","15.0","15.0","","","18.5","19.9","21.0","22.4"]
["","C Condition (7°C)","","COPd (declared COP)","","5.35","","","6.39","5.24","6.45","5.57","6.41","5.78","6.19","","","6.10","5.97","6.42","6.40"]
["","","","Pdh (declared heating cap)","kW","4.76","","","6.36","8.54","7.14","8.08","8.04","9.65","9.65","","","11.9","12.8","13.5","14.4"]
["","D Condition (12°C)","","COPd (declared COP)","","7.04","","","9.39","6.58","6.94","6.97","6.47","7.59","8.15","","","8.60","6.72","8.03","7.72"]
["","","","Pdh (declared heating cap)","kW","4.71","","","5.80","9.17","5.33","9.24","5.36","10.3","7.68","","","11.4","10.1","11.1","11.2"]
["","TBivalent","","COPd (declared COP)","","2.73","","","2.38","2.26","2.58","2.38","2.54","2.27","2.28","","","2.26","2.17","2.24","2.20"]
["","","","Pdh (declared heating cap)","kW","13.7","","","18.4","21.7","20.6","23.2","23.2","27.9","27.9","","","34.4","36.9","39.0","41.6"]
["","","","Tbiv (bivalent temperature)","°C","-10","","","-10","-10","-10","-10","-10","-10","-10","","","-10","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","2.73","","","2.38","2.26","2.58","2.38","2.54","2.27","2.28","","","2.26","2.17","2.24","2.20"]
["","","","Pdh (declared heating cap)","kW","13.7","","","18.4","21.7","20.6","23.2","23.2","27.9","27.9","","","34.4","36.9","39.0","41.6"]
["","","","Tol (temperature operating limit)","°C","-10","","","-10","-10","-10","-10","-10","-10","-10","","","-10","-10","-10","-10"]
["Space heating (Average climate) recommended combination 3","A Condition (-7°C)","","COPd (declared COP)","","3.05","","","2.85","3.07","2.96","3.17","2.88","2.91","2.73","","","2.77","2.95","2.91","2.87"]
["","","","Pdh (declared heating cap)","kW","12.1","","","16.3","19.2","18.2","20.5","20.5","24.7","24.8","","","30.5","32.7","34.6","36.9"]
["","B Condition (2°C)","","COPd (declared COP)","","3.86","","","4.24","4.14","3.89","4.19","3.95","4.35","4.25","","","4.28","3.92","4.05","4.08"]
["","","","Pdh (declared heating cap)","kW","7.39","","","9.89","11.7","11.1","12.5","12.5","15.0","15.0","","","18.5","19.9","21.0","22.4"]
["","C Condition (7°C)","","COPd (declared COP)","","5.35","","","6.43","5.25","6.43","5.52","6.34","5.77","6.39","","","6.12","5.93","6.43","6.38"]
["","","","Pdh (declared heating cap)","kW","4.75","","","6.36","8.49","7.15","8.04","8.03","9.67","9.66","","","11.9","12.8","13.5","14.4"]
["","D Condition (12°C)","","COPd (declared COP)","","7.14","","","9.37","6.64","6.84","6.94","6.44","7.69","5.48","","","8.65","6.75","7.95","7.68"]
["","","","Pdh (declared heating cap)","kW","4.65","","","5.67","9.13","5.29","9.17","5.32","10.2","5.80","","","11.2","9.97","11.0","11.0"]
["","TBivalent","","COPd (declared COP)","","2.78","","","2.41","2.78","2.58","2.86","2.54","2.53","2.39","","","2.35","2.62","2.50","2.48"]
["","","","Pdh (declared heating cap)","kW","13.7","","","18.4","21.7","20.6","23.2","23.2","27.9","28.0","","","34.4","36.9","39.0","41.6"]
["","","","Tbiv (bivalent temperature)","°C","-10","","","-10","-10","-10","-10","-10","-10","-10","","","-10","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","2.78","","","2.41","2.78","2.58","2.86","2.54","2.53","2.39","","","2.35","2.62","2.50","2.48"]
["","","","Pdh (declared heating cap)","kW","13.7","","","18.4","21.7","20.6","23.2","23.2","27.9","28.0","","","34.4","36.9","39.0","41.6"]
["","","","Tol (temperature operating limit)","°C","-10","","","-10","-10","-10","-10","-10","-10","-10","","","-10","-10","-10","-10"]
["Capacity range","HP","","","","8","10","10","12","13","14","16","16","18","18","20","20","22","24","26","28"]
["Maximum number of connectable indoor units","","","","","64 (3)","64","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)"]
["Indoor index connection","Min.","","","","100","","","150","163","175","200","200","225","225","","","275","300","325","350"]
["","Max.","","","","260","","","390","423","455","520","520","585","585","","","715","780","845","910"]
["Dimensions","Unit","","Height","mm","1,685","","","1,685","","1,685","","1,685","","1,685"]
["","","","Width","mm","930","","","930","","1,240","","1,240","","1,240"]
["","","","Depth","mm","765","","","765","","765","","765","","765"]
["Weight","Unit","","","kg","213","","","213","","296","","296","","319"]
["Fan","External static pressure","","Max.","Pa","78","","","78","","78","","78","","78"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","","","Hermetically sealed scroll compressor","","Hermetically sealed scroll compressor","","Hermetically sealed scroll compressor","","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","-5","","","-5","","-5","","-5","","-5"]
["","","","Max.","°CDB","46","","","46","","46","","46","","46"]
["","Heating","","Min.","°CWB","-20","","","-20","","-20","","-20","","-20"]
["","","","Max.","°CWB","16","","","16","","16","","16","","16"]
["Sound power level","Cooling","","Nom.","dBA","78.3 (5)","","","82.5 (5)","81.3 (5)","78.7 (5)","81.3 (5)","83.7 (5)","81.6 (5)","83.4 (5)","","","84.0 (5)","84.8 (5)","84.0 (5)","86.2 (5)"]
["Sound pressure level","Cooling","","Nom.","dBA","56.3 (6)","","","60.8 (6)","59.3 (6)","58.1 (6)","59.3 (6)","61.4 (6)","60.2 (6)","63.0 (6)","","","62.6 (6)","62.6 (6)","62.7 (6)","64.1 (6)"]
["Refrigerant","Type","","","","R-32","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","","","R-32","R-32","R-32","R-32"]
["","GWP","","","","675.0","","","675.0","675.0","675.0","675.0","675.0","675.0","675.0","","","675.0","675.0","675.0","675.0"]
["","Charge","","","kg","9.00","","","9.00","","10.6","","10.6","","10.6"]
["Piping connections","Liquid","","Type","","Braze connection","","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","","","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","9.52","","","12.70","12.70","12.70","12.70","12.70","12.70","12.70","","","12.70","12.70","15.90","15.90"]
["","Gas","","Type","","Braze connection","","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","","","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","19.1","","","22.2","22.2","22.2","22.2","22.2","22.2","22.2","","","28.6","28.6","28.6","28.6"]
["","HP/LP gas","","OD","mm","15.90","","","19.10","19.10","19.10","19.10","19.10","19.10","19.10","","","22.20","22.20","22.20","22.20"]
["","Total piping length","System","Actual","m","1,000 (7)","","","1,000 (7)","500 (7)","1,000 (7)","500 (7)","1,000 (7)","500 (7)","1,000 (7)","","","1,000 (7)","1,000 (7)","1,000 (7)","1,000 (7)"]
["Standard Accessories","Installation and operation manual","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Connection pipes","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["Power supply","Name","","","","Y1","","","Y1","Y1","Y1","Y1","Y1","Y1","Y1","","","Y1","Y1","Y1","Y1"]
["","Phase","","","","3N~","","","3N~","3N~","3N~","3N~","3N~","3N~","3N~","","","3N~","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","","","50","50","50","50","50","50","50","","","50","50","50","50"]
["","Voltage","","","V","380-415","","","380-415","380-415","380-415","380-415","380-415","380-415","380-415","","","380-415","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system."]
["","","","","","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of"]
["","","","","","(5) - Sound power level is an absolute value that a sound source generates.","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(7) - Refer to refrigerant pipe selection or installation manual","","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","","","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","","","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","","","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(13) - Maximum allowable voltage range variation between phases is 2%.","","","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","","","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(15) - Sound values are measured in a semi-anechoic room.","","","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","","","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room."]
["","","","","","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","","","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","","","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(17) - Ssc: Short-circuit power","","","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","","","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power"]
["","","","","","(18) - For detailed contents of standard accessories, see installation/operation manual","","","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","","","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","","","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","","","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~28HP) data is corresponding with the standard multi combination"]
["System","Outdoor unit module 1","","","","","REMA5A","","","","","","","","","","REYA8A"]
["","Outdoor unit module 2","","","","","REMA5A","","","","","","","","","","REYA12A"]
["Cooling capacity","Prated,c","","","kW","","28","28","","","","","","","","56","55.9 (1)"]
["Heating capacity","Prated,h","","","kW","","28","28","","","","","","","","56","55.9 (2)"]
["","Nom.","","6°CWB","kW","","28","28","","","","","","","","56","55.9 (2)"]
["COP at nom. capacity","6°CWB","","","KW/KW","","3.66","3.45 (2)","","","","","","","","3.37 (2)","3.6"]
["Space cooling","A Condition (35°C - 27/19)","","EERd","","","3.81","3.26","","","","","","","","2.57","3.24"]
["","","","Pdc","kW","","28","28.0","","","","","","","","56.0","55.9"]
["","B Condition (30°C - 27/19)","","EERd","","","7.73","5.00","","","","","","","","4.42","4.89"]
["","","","Pdc","kW","","20.6","20.6","","","","","","","","41.3","41.2"]
["","C Condition (25°C - 27/19)","","EERd","","","8.99","8.50","","","","","","","","7.70","8.7"]
["","","","Pdc","kW","","13.5","13.3","","","","","","","","26.5","26.5"]
["","D Condition (20°C - 27/19)","","EERd","","","11.5","14.8","","","","","","","","15.8","16.4"]
["","","","Pdc","kW","","14.1","8.19","","","","","","","","11.6","16.7"]
["Space cooling recommended combination 2","A Condition (35°C - 27/19)","","EERd","","","3.67","3.23","","","","","","","","2.52","3.09"]
["","","","Pdc","kW","","28","28","","","","","","","","56","55.9"]
["","B Condition (30°C - 27/19)","","EERd","","","7.32","4.83","","","","","","","","4.41","4.75"]
["","","","Pdc","kW","","20.6","20.6","","","","","","","","41.3","41.2"]
["","C Condition (25°C - 27/19)","","EERd","","","8.54","8.06","","","","","","","","7.41","8.17"]
["","","","Pdc","kW","","13.3","13.3","","","","","","","","26.5","26.5"]
["","D Condition (20°C - 27/19)","","EERd","","","11.1","14.1","","","","","","","","16.6","15.7"]
["","","","Pdc","kW","","13.7","7.97","","","","","","","","11.9","16"]
["Space cooling recommended combination 3","A Condition (35°C - 27/19)","","EERd","","","3.71","3.27","","","","","","","","2.50","3.27"]
["","","","Pdc","kW","","28.0","28.0","","","","","","","","56.0","55.9"]
["","B Condition (30°C - 27/19)","","EERd","","","7.71","4.91","","","","","","","","4.41","5.04"]
["","","","Pdc","kW","","20.6","20.6","","","","","","","","41.3","41.2"]
["","C Condition (25°C - 27/19)","","EERd","","","8.99","8.59","","","","","","","","7.71","9.03"]
["","","","Pdc","kW","","13.5","13.3","","","","","","","","26.5","26.5"]
["","D Condition (20°C - 27/19)","","EERd","","","11.6","15.1","","","","","","","","16.4","16.9"]
["","","","Pdc","kW","","14.1","8.13","","","","","","","","11.8","16.7"]
["Space heating (Average climate)","TBivalent","","COPd (declared COP)","","","2.69","2.28","","","","","","","","2.23","2.55"]
["","","","Pdh (declared heating cap)","kW","","16","16.0","","","","","","","","31.0","31"]
["","","","Tbiv (bivalent temperature)","°C","","-10","-10","","","","","","","","-10","-10"]
["","Space heating (Average climate)-=-E condition (-10°C)","","Space heating (Average climate)-=-E condition (-10°C)-=-COPd (declared COP)","","","2.69","2.28","","","","","","","","2.23","2.55"]
["","","","Space heating (Average climate)-=-E condition (-10°C)-=-Pdh (declared heating cap)-=-kW","kW","","16","16.0","","","","","","","","31.0","31"]
["","TOL","","Tol (temperature operating limit)","°C","","-10","-10","","","","","","","","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","","3","2.67","","","","","","","","2.60","2.95"]
["","","","Pdh (declared heating cap)","kW","","14.2","14.2","","","","","","","","27.4","27.4"]
["","B Condition (2°C)","","COPd (declared COP)","","","4.37","4.23","","","","","","","","3.84","4.09"]
["","","","Pdh (declared heating cap)","kW","","8.6","8.62","","","","","","","","16.7","16.7"]
["","C Condition (7°C)","","COPd (declared COP)","","","4.7","5.70","","","","","","","","5.89","5.9"]
["","","","Pdh (declared heating cap)","kW","","7.17","5.54","","","","","","","","10.7","10.7"]
["","D Condition (12°C)","","COPd (declared COP)","","","5.57","7.92","","","","","","","","7.70","8.06"]
["","","","Pdh (declared heating cap)","kW","","8.74","5.46","","","","","","","","7.34","10"]
["Space heating (Average climate) recommended combination 2","TBivalent","","COPd (declared COP)","","","2.7","2.32","","","","","","","","2.18","2.34"]
["","","","Pdh (declared heating cap)","kW","","16","16","","","","","","","","31","31"]
["","","","Tbiv (bivalent temperature)","°C","","-10","-10","","","","","","","","-10","-10"]
["","TOL","","COPd (declared COP)","","","2.7","2.32","","","","","","","","2.18","2.34"]
["","","","Pdh (declared heating cap)","kW","","16","16","","","","","","","","31","31"]
["","","","Tol (temperature operating limit)","°C","","-10","-10","","","","","","","","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","","3.02","2.62","","","","","","","","2.54","2.96"]
["","","","Pdh (declared heating cap)","kW","","14.2","14.2","","","","","","","","27.5","27.4"]
["","B Condition (2°C)","","COPd (declared COP)","","","4.43","4.24","","","","","","","","3.79","4.21"]
["","","","Pdh (declared heating cap)","kW","","8.64","8.61","","","","","","","","16.7","16.7"]
["","C Condition (7°C)","","COPd (declared COP)","","","4.76","5.79","","","","","","","","5.98","6.07"]
["","","","Pdh (declared heating cap)","kW","","7.31","5.54","","","","","","","","10.7","10.7"]
["","D Condition (12°C)","","COPd (declared COP)","","","5.62","7.91","","","","","","","","7.81","8.3"]
["","","","Pdh (declared heating cap)","kW","","8.87","5.6","","","","","","","","7.69","10.5"]
["Space heating (Average climate) recommended combination 3","TBivalent","","COPd (declared COP)","","","2.71","2.29","","","","","","","","2.24","2.59"]
["","","","Pdh (declared heating cap)","kW","","16.0","16.0","","","","","","","","31.1","31.0"]
["","","","Tbiv (bivalent temperature)","°C","","-10","-10","","","","","","","","-10","-10"]
["","TOL","","COPd (declared COP)","","","2.71","2.29","","","","","","","","2.24","2.59"]
["","","","Pdh (declared heating cap)","kW","","16.0","16.0","","","","","","","","31.1","31.0"]
["","","","Tol (temperature operating limit)","°C","","-10","-10","","","","","","","","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","","3.03","2.68","","","","","","","","2.60","2.99"]
["","","","Pdh (declared heating cap)","kW","","14.2","14.2","","","","","","","","27.5","27.5"]
["","B Condition (2°C)","","COPd (declared COP)","","","4.48","4.32","","","","","","","","3.88","4.22"]
["","","","Pdh (declared heating cap)","kW","","8.61","8.62","","","","","","","","16.7","16.7"]
["","C Condition (7°C)","","COPd (declared COP)","","","4.76","5.80","","","","","","","","6.07","6.07"]
["","","","Pdh (declared heating cap)","kW","","7.28","5.55","","","","","","","","10.7","10.7"]
["","D Condition (12°C)","","COPd (declared COP)","","","5.62","8.02","","","","","","","","6.15","8.32"]
["","","","Pdh (declared heating cap)","kW","","8.85","5.56","","","","","","","","5.91","10.3"]
["Indoor index connection","Min.","","","","","125","125","","","","","","","","250","250"]
["","Max.","","","","","325","325","","","","","","","","650","650"]
["Sound power level","Cooling","","Nom.","dBA","","81.3","78.8 (5)","","","","","","","","87.9 (5)","83.9 (5)"]
["Sound pressure level","Cooling","","Nom.","dBA","","59.3","58","","","","","","","","67","62.1 (6)"]
["Refrigerant","Type","","","","","R-32","R-32","","","","","","","","R-32","R-32"]
["","GWP","","","","","675","675.0","","","","","","","","675.0","675"]
["Piping connections","Liquid","","Type","","","Braze connection","Braze connection","","","","","","","","Braze connection","Braze connection"]
["","","","OD","mm","","9.52","9.52","","","","","","","","12.7","12.7"]
["","Gas","","Type","","","Braze connection","Braze connection","","","","","","","","Braze connection","Braze connection"]
["","","","OD","mm","","19.1","19.1","","","","","","","","28.6","28.6"]
["","HP/LP gas","","OD","mm","","15.90","15.90","","","","","","","","22.20","22.20"]
["","Total piping length","System","Actual","m","","500","1000 (7)","","","","","","","","1000 (7)","500 (7)"]
["Power supply","Name","","","","","Y1","Y1","","","","","","","","Y1","Y1"]
["","Phase","","","","","3N~","3N~","","","","","","","","3N~","3N~"]
["","Frequency","","","Hz","","50","50","","","","","","","","50","50"]
["","Voltage","","","V","","380-415","380-415","","","","","","","","380-415","380-415"]
["Dimensions","Unit","","Height","mm","","","1685","","","","","","","","1685"]
["","","","Width","mm","","","930","","","","","","","","1240"]
["","","","Depth","mm","","","765","","","","","","","","765"]
["Weight","Unit","","","kg","","","213","","","","","","","","319"]
["Fan","External static pressure","","Max.","Pa","","","78","","","","","","","","78"]
["Compressor","Type","","","","","","Hermetically sealed scroll compressor","","","","","","","","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","","","-5","","","","","","","","-5"]
["","","","Max.","°CDB","","","46","","","","","","","","46"]
["","Heating","","Min.","°CWB","","","-20","","","","","","","","-20"]
["","","","Max.","°CWB","","","16","","","","","","","","16"]
["Refrigerant","Charge","","","tCO2Eq","","","6.08","","","","","","","","7.16"]
["","Charge","","","kg","","","9","","","","","","","","10.6"]