{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":38,"n_cols":15,"rows_kept":38,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXM-R"]
[]
[]
[]
[]
["","","","","","RXM20R5V1B","RXM25R5V1B","RXM35R5V1B","RXM42R2V1B","RXM42R5V1B","RXM50R5V1B","RXM50R2V1B","RXM60R2V1B","RXM60R5V1B","RXM71R2V1B"]
["Dimensions","Unit","","Height","mm","552","552","552","734","734","734","734","734","734","734"]
["","","","Width","mm","840","840","840","954","954","954","954","954","954","954"]
["","","","Depth","mm","350","350","350","401","401","401","401","401","401","401"]
["Weight","Unit","","","kg","32","32","32","49.0","49.0","49.0","49.0","49.0","49.0","55"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Operation range","Cooling","Ambient","Min.","°CDB","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","50 (4), 46 (5)","50 (4), 46 (5)","50 (4), 46 (5)","50, 46","50, 46","50, 46","50, 46","50, 46","50, 46","46"]
["","Heating","Ambient","Min.","°CWB","-15","-15","-15","-15","-21","-21","-15","-15","-21","-15"]
["","","","Max.","°CWB","18","18","18","18","18","18","18","18","18","18"]
["Sound pressure level","Cooling","","Nom.","dBA","46","46","49","48.0","48.0","48.0","48.0","48.0","48.0","47.0"]
["","Heating","","Nom.","dBA","47","47","49","48.0","48.0","49.0","49.0","49.0","49.0","48.0"]
["Refrigerant","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Charge","","","kg","0.76","0.76","0.76","1.10","1.10","1.15","1.15","1.15","1.15","1.15"]
["","Charge","","","tCO2Eq","0.52","0.52","0.52","0.750","0.750","0.780","0.780","0.780","0.780","0.780"]
["","GWP","","","","675","675","675","675.0","675.0","675.0","675.0","675.0","675.0","675.0"]
["Piping connections","Piping length","OU - IU","Max.","m","20","20","20","30","30","30","30","30","30","30"]
["","Additional refrigerant charge","","","kg/m","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)"]
["","Level difference","IU - OU","Max.","m","15","15","15","20.0","20.0","20.0","20.0","20.0","20.0","20.0"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1","1","1","1"]
["","Refrigerant charge label","","","","1","1","1","1","1","1","1","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1","1","1","1","1","1","1","1"]
["","Drain plug","","","","1","1","1","1","1","1","1","1","1","1"]
["Energy Efficiency Range","","","","","A+++ ~ D","A+++ ~ D","A+++ ~ D","A+++ ~ D","A+++ ~ D","A+++ ~ D","A+++ ~ D","A+++ ~ D","A+++ ~ D","A+++ ~ D"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Contains fluorinated greenhouse gases","(1) - Contains fluorinated greenhouse gases","(1) - Contains fluorinated greenhouse gases","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range"]
["","","","","","(2) - See separate drawing for operation range","(2) - See separate drawing for operation range","(2) - See separate drawing for operation range","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data"]
["","","","","","(3) - See separate drawing for electrical data","(3) - See separate drawing for electrical data","(3) - See separate drawing for electrical data","(3) - Contains fluorinated greenhouse gases","(3) - Contains fluorinated greenhouse gases","(3) - Contains fluorinated greenhouse gases","(3) - Contains fluorinated greenhouse gases","(3) - Contains fluorinated greenhouse gases","(3) - Contains fluorinated greenhouse gases","(3) - Contains fluorinated greenhouse gases"]
["","","","","","(4) - Only possible in combination with CTXM*N2V1B, ATXM*N2V1B, FTXM*N2V1B","(4) - Only possible in combination with CTXM*N2V1B, ATXM*N2V1B, FTXM*N2V1B","(4) - Only possible in combination with CTXM*N2V1B, ATXM*N2V1B, FTXM*N2V1B"]
["","","","","","(5) - Only possible in combination with CTXM*M2V1B, ATXM*M2V1B, FTXM*M2V1B, FVXM*FV1B, FCAG*AVEB, FFA*A2VEB9,FBA*A2VEB9, FHA*AVEB9, FDXM*F3V1B9, FNA*A2VEB9, ADEA*A2VEB·","(5) - Only possible in combination with CTXM*M2V1B, ATXM*M2V1B, FTXM*M2V1B, FVXM*FV1B, FCAG*AVEB, FFA*A2VEB9,FBA*A2VEB9, FHA*AVEB9, FDXM*F3V1B9, FNA*A2VEB9, ADEA*A2VEB·","(5) - Only possible in combination with CTXM*M2V1B, ATXM*M2V1B, FTXM*M2V1B, FVXM*FV1B, FCAG*AVEB, FFA*A2VEB9,FBA*A2VEB9, FHA*AVEB9, FDXM*F3V1B9, FNA*A2VEB9, ADEA*A2VEB·"]
["Standard Accessories","Drain cap","","","","","","","3","3","3","3","3","3","3"]