{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":6,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXMLQ-T"]
[]
[]
[]
[]
["","","","","","RXMLQ8T7Y1B"]
["Sound pressure level","Cooling","","Nom.","dBA","55.0 (5)"]
["Standard Accessories","Installation manual","","","","1"]
["","Operation manual","","","","2"]
["","Connection pipes","","","","25"]
["Operation range","Cooling","","Max.","°CDB","43"]
["","","","Min.","°CDB","-5"]
["","Heating","","Min.","°CWB","-25"]
["","","","Max.","°CWB","16"]
["Compressor","Type","","","","Hermetically sealed scroll compressor"]
["Weight","Unit","","","kg","302"]
["Refrigerant","Charge","","","TCO2Eq","24.6"]
["","GWP","","","","2,087.5"]
["","Charge","","","kg","11.8"]
["","Type","","","","R-410A"]
["Piping connections","Liquid","","OD","mm","10"]
["","","","Type","","Braze connection"]
["","Total piping length","System","Actual","m","500 (6)"]
["","Gas","","OD","mm","19.1"]
["","","","Type","","Braze connection"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","50"]
["","","","Indoor unit in highest position","m","40"]
["","","IU - IU","Max.","m","30"]
["Sound power level","Cooling","","Nom.","dBA","75.0 (4)"]
["Dimensions","Unit","","Width","mm","1,240"]
["","","","Depth","mm","765"]
["","","","Height","mm","1,685"]
["Fan","External static pressure","","Max.","Pa","78"]
["Power supply","Phase","","","","3N~"]
["","Name","","","","Y1"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal); level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (70% <= CR <= 130%)"]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(12) - TOCA means the total value of each OC set."]
["","","","","","(13) - FLA means the nominal running current of the fan"]