{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":142,"n_cols":11,"rows_kept":142,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYSA-AY1"]
[]
[]
[]
[]
["","","","","","RXYSA4A7Y1B","RXYSA5A7Y1B","RXYSA6A7Y1B","RXYSA8AMY1B","RXYSA10AMY1B","RXYSA12AMY1B"]
["Recommended combination","","","","","3 x FXSA25A2VEB + 1 x FXSA32A2VEB","4 x FXSA32A2VEB","2 x FXSA32A2VEB + 2 x FXSA40A2VEB","4 x FXSA50A2VEB","4 x FXSA63A2VEB","6 x FXSA50A2VEB"]
["Recommended combination 2","","","","","","","","4 x FXFA50A2VEB","4 x FXFA63A2VEB","6 x FXFA50A2VEB"]
["Recommended combination 3","","","","","","","","4 x FXMA50A5VEB","4 x FXMA63A5VEB","6 x FXMA50A5VEB"]
["Cooling capacity","Prated,c","","","kW","12.1 (1)","14","15.5 (1)","22.4 (1)","28","33.5 (1)"]
["Heating capacity","Prated,h","","","kW","12.1 (2)","14","15.5 (2)","22.4 (2)","28","33.5 (2)"]
["","Nom.","","6°CWB","kW","12.1 (2)","14","15.5 (2)","22.4 (2)","28","33.5 (2)"]
["COP at nom. capacity","6°CWB","","","KW/KW","4.49","4.2","4.1","3.47 (2)","3.83 (2)","3.82 (2)"]
["SEER","","","","","7.9","7.4","7.3","6.36","6.93","6.47"]
["SEER recommended combination 2","","","","","","","","7.14","7.13","7.07"]
["SEER recommended combination 3","","","","","","","","6.86","7.04","6.88"]
["SCOP","","","","","4.9","4.5","4.5","4.42","4.42","4.64"]
["SCOP recommended combination 2","","","","","","","","4.44","4.42","4.66"]
["SCOP recommended combination 3","","","","","","","","4.46","4.46","4.7"]
["Space cooling","A Condition (35°C - 27/19)","","EERd","","3.4","3.1","3.0","2.38","2.94","2.47"]
["","","","Pdc","kW","12.1","14.0","15.5","22.4","28","33.5"]
["","B Condition (30°C - 27/19)","","EERd","","5.6","5.1","4.8","4.09","4.9","4.39"]
["","","","Pdc","kW","8.9","10.3","11.4","16.5","20.6","24.7"]
["","C Condition (25°C - 27/19)","","EERd","","10.4","9.5","9.3","7.56","7.21","6.86"]
["","","","Pdc","kW","5.7","6.6","7.3","10.6","13.3","15.9"]
["","D Condition (20°C - 27/19)","","EERd","","17.5","17.5","17.9","17.33","18.5","19.2"]
["","","","Pdc","kW","4.9","4.5","4.9","4.7","5.9","7.1"]
["Space cooling recommended combination 2","A Condition (35°C - 27/19)","","EERd","","","","","2.86","3","2.88"]
["","","","Pdc","kW","","","","22.4","28","33.5"]
["","B Condition (30°C - 27/19)","","EERd","","","","","4.74","4.99","4.69"]
["","","","Pdc","kW","","","","16.5","20.6","24.7"]
["","C Condition (25°C - 27/19)","","EERd","","","","","8.42","7.73","7.71"]
["","","","Pdc","kW","","","","10.6","13.3","15.9"]
["","D Condition (20°C - 27/19)","","EERd","","","","","18.05","18.82","20.08"]
["","","","Pdc","kW","","","","5.3","7.3","7.8"]
["Space cooling recommended combination 3","A Condition (35°C - 27/19)","","EERd","","","","","2.62","3.04","2.68"]
["","","","Pdc","kW","","","","22.4","28","33.5"]
["","B Condition (30°C - 27/19)","","EERd","","","","","4.63","4.77","4.54"]
["","","","Pdc","kW","","","","16.5","20.6","24.7"]
["","C Condition (25°C - 27/19)","","EERd","","","","","8.07","7.21","7.51"]
["","","","Pdc","kW","","","","10.6","13.3","15.9"]
["","D Condition (20°C - 27/19)","","EERd","","","","","16.98","21.9","19.98"]
["","","","Pdc","kW","","","","5.1","7.1","7.1"]
["Space heating (Average climate)","TBivalent","","COPd (declared COP)","","2.7","2.5","2.4","2.21","2.23","2.2"]
["","","","Pdh (declared heating cap)","kW","8.4","9.7","10.7","14.9","19.6","23.5"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10","-10","-10","-10"]
["","Space heating (Average climate)-=-E condition (-10°C)","","Space heating (Average climate)-=-E condition (-10°C)-=-COPd (declared COP)","","2.7","2.5","2.4","2.21","2.23","2.2"]
["","","","Space heating (Average climate)-=-E condition (-10°C)-=-Pdh (declared heating cap)-=-kW","kW","8.4","9.7","10.7","14.9","19.6","23.5"]
["","TOL","","Tol (temperature operating limit)","°C","-10","-10","-10","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","3.3","2.8","2.8","2.52","2.62","2.71"]
["","","","Pdh (declared heating cap)","kW","7.4","8.5","9.5","13.2","17.4","20.8"]
["","B Condition (2°C)","","COPd (declared COP)","","4.7","4.3","4.1","4.32","4.47","4.63"]
["","","","Pdh (declared heating cap)","kW","4.5","5.2","5.8","8","10.6","12.7"]
["","C Condition (7°C)","","COPd (declared COP)","","6.8","6.5","6.5","6.32","6.16","6.51"]
["","","","Pdh (declared heating cap)","kW","3.3","3.3","3.7","5.2","6.8","8.1"]
["","D Condition (12°C)","","COPd (declared COP)","","8.6","8.4","8.7","6.95","5.56","6.34"]
["","","","Pdh (declared heating cap)","kW","3.9","3.9","4.0","2.9","4.7","4.8"]
["Space heating (Average climate) recommended combination 2","TBivalent","","COPd (declared COP)","","","","","2.31","2.3","2.18"]
["","","","Pdh (declared heating cap)","kW","","","","14.9","19.6","23.5"]
["","","","Tbiv (bivalent temperature)","°C","","","","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","","","","2.31","2.3","2.18"]
["","","","Pdh (declared heating cap)","kW","","","","14.9","19.6","23.5"]
["","","","Tol (temperature operating limit)","°C","","","","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","","","","2.6","2.7","2.77"]
["","","","Pdh (declared heating cap)","kW","","","","13.2","17.4","20.8"]
["","B Condition (2°C)","","COPd (declared COP)","","","","","4.42","4.45","4.66"]
["","","","Pdh (declared heating cap)","kW","","","","8","10.6","12.7"]
["","C Condition (7°C)","","COPd (declared COP)","","","","","6.08","6.05","6.46"]
["","","","Pdh (declared heating cap)","kW","","","","5.2","6.8","8.1"]
["","D Condition (12°C)","","COPd (declared COP)","","","","","6.6","5.52","6.11"]
["","","","Pdh (declared heating cap)","kW","","","","2.9","4.5","4.5"]
["Space heating (Average climate) recommended combination 3","TBivalent","","COPd (declared COP)","","","","","2.25","2.27","2.18"]
["","","","Pdh (declared heating cap)","kW","","","","14.9","19.6","23.5"]
["","","","Tbiv (bivalent temperature)","°C","","","","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","","","","2.25","2.27","2.18"]
["","","","Pdh (declared heating cap)","kW","","","","14.9","19.6","23.5"]
["","","","Tol (temperature operating limit)","°C","","","","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","","","","2.56","2.7","2.77"]
["","","","Pdh (declared heating cap)","kW","","","","13.2","17.4","20.8"]
["","B Condition (2°C)","","COPd (declared COP)","","","","","4.4","4.47","4.69"]
["","","","Pdh (declared heating cap)","kW","","","","8","10.6","12.7"]
["","C Condition (7°C)","","COPd (declared COP)","","","","","6.26","6.19","6.54"]
["","","","Pdh (declared heating cap)","kW","","","","5.2","6.8","8.1"]
["","D Condition (12°C)","","COPd (declared COP)","","","","","7.11","5.72","6.48"]
["","","","Pdh (declared heating cap)","kW","","","","3.2","4.7","4.9"]
["Capacity range","HP","","","","4","5","6","8","10","12"]
["Maximum number of connectable indoor units","","","","","13 (3)","16 (3)","18 (3)","26 (3)","32 (3)","39 (3)"]
["Indoor index connection","Min.","","","","50","62.5","70","100","125","150"]
["","Nom.","","","","100","125","140"]
["","Max.","","","","130","162.5","182","260","325","390"]
["Dimensions","Unit","","Height","mm","869","869","869","1,430","1,615","1,615"]
["","","","Width","mm","1,100","1,100","1,100","940","940","940"]
["","","","Depth","mm","460","460","460","320","460","460"]
["Weight","Unit","","","kg","102","102","102","134","163","163"]
["Fan","External static pressure","","Max.","Pa","45","45","45","35","35","35"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","-5","-5","-5","-5","-5","-5"]
["","","","Max.","°CDB","46","46","46","52","52","52"]
["","Heating","","Min.","°CWB","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°CWB","16","16","16","15.5","15.5","15.5"]
["Sound power level","Cooling","","Nom.","dBA","67.0 (4)","68.1 (4)","69.0 (4)","73.2 (4)","74","76.1 (4)"]
["Sound pressure level","Cooling","","Nom.","dBA","49","51","51","58.1 (5)","57","60"]
["Refrigerant","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32"]
["","GWP","","","","675.0","675.0","675.0","675","675","675"]
["","Charge","","","tCO2Eq","2.3","2.3","2.3","3.51","4.73","4.79"]
["","Charge","","","kg","3.4","3.4","3.4","5.2","7","7.1"]
["Piping connections","Liquid","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","9.52","9.52","9.52","9.52","9.52","12.7"]
["","Gas","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","15.9","15.9","15.9","19.1","19.1","22.2"]
["","Total piping length","System","Actual","m","300 (7)","300 (7)","300 (7)","300 (6)","300 (6)","300 (6)"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","50","50","50"]
["","","","Indoor unit in highest position","m","40","40","40"]
["Standard Accessories","Caution label","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","Auxiliary piping set","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","Peel off F-gas label","","","","1","1","1"]
["","Installation and operation manual","","","","1","1","1","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Power supply","Name","","","","Y1","Y1","Y1","Y1","Y1","Y1"]
["","Phase","","","","3N~","3N~","3N~","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","50","50","50/60","50/60","50/60"]
["","Voltage","","","V","380-415","380-415","380-415","380-415/400","380-415/400","380-415/400"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system."]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - According to ENER Lot 21","(5) - According to ENER Lot 21","(5) - According to ENER Lot 21","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(11) - TOCA means the total value of each OC set.","(11) - TOCA means the total value of each OC set.","(11) - TOCA means the total value of each OC set.","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(12) - FLA means the nominal running current of the fan","(12) - FLA means the nominal running current of the fan","(12) - FLA means the nominal running current of the fan","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%."]
["Standard Accessories","Connection pipes","","","","","","","1","2","1"]
["Notes","","","","","","","","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","","","","(14) - Sound values are measured in a semi-anechoic room.","(14) - Sound values are measured in a semi-anechoic room.","(14) - Sound values are measured in a semi-anechoic room."]
["","","","","","","","","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","","","","(16) - Ssc: Short-circuit power","(16) - Ssc: Short-circuit power","(16) - Ssc: Short-circuit power"]
["","","","","","","","","(17) - For detailed contents of standard accessories, see installation/operation manual","(17) - For detailed contents of standard accessories, see installation/operation manual","(17) - For detailed contents of standard accessories, see installation/operation manual"]