{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":12,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-NY1"]
[]
[]
[]
[]
["","","","","","RZAG71N2Y1B","RZAG71N7Y1B","RZAG100N7Y1B","RZAG100N2Y1B","RZAG125N7Y1B","RZAG140N7Y1B","RZAG140N2Y1B"]
["Dimensions","Unit","","Height","mm","870","870","870","870","870","870","870"]
["","","","Width","mm","1100","1100","1100","1100","1100","1100","1100"]
["","","","Depth","mm","460","460","460","460","460","460","460"]
["Weight","Unit","","","kg","81","81","85","85","94","94","94"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Operation range","Cooling","Ambient","Min.","°CDB","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°CDB","52","52","52","52","52","52","52"]
["","Heating","Ambient","Min.","°CWB","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°CWB","18","18","18","18","18","18","18"]
["Sound power level","Cooling","","","dBA","64","64","66","66","69","70","70"]
["","Heating","","","dBA","","","","","68 (1)","71 (1)","71 (1)"]
["Sound pressure level","Cooling","","Nom.","dBA","46","46","47","47","49","50","50"]
["","Heating","","Nom.","dBA","48","48","50","50","52","52","52"]
["Refrigerant","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Charge","","","kg","3.20","3.2","3.2","3.20","3.7","3.7","3.70"]
["","GWP","","","","675","675","675","675","675","675","675"]
["","Charge","","","tCO2Eq","2.16","2.16","2.16","2.16","2.5","2.5","2.50"]
["Piping connections","Liquid","","OD","mm","10","10","10","10","10","10","10"]
["","Gas","","OD","mm","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["","Piping length","OU - IU","Max.","m","55","55","85","85","85","85","85"]
["","","System","Equivalent","m","75","75","100","100","100","100","100"]
["","","","Chargeless","m","40","40","40","40","40","40","40"]
["","Additional refrigerant charge","","","kg/m","See installation manual","See installation manual","See installation manual","See installation manual","See installation manual","See installation manual","See installation manual"]
["","Level difference","IU - OU","Max.","m","30","30","30","30","30","30","30"]
["","","IU - IU","Max.","m","0.5","0.5","0.5","0.5","0.5","0.5","0.5"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1","1","1","1"]
["","Peel off F-gas label","","","","1","1","1","1","1","1","1"]
["","Tie-wraps","","","","2","2","2","2","2","2","2"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","16","16","16","16","16","16"]
["Notes","","","","","","","","","(1) - According to ENER Lot 21","(1) - According to ENER Lot 21","(1) - According to ENER Lot 21"]