{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":18,"n_cols":8,"rows_kept":18,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","SEHVX-AAW / SERHQ-AAW1"]
[]
[]
[]
[]
["","","","","SEHVX20AAW / SERHQ020AAW1","SEHVX32AAW / SERHQ032AAW1","SEHVX40AAW / SERHQ020AAW1+SERHQ020AAW1","SEHVX64AAW / SERHQ032AAW1+SERHQ032AAW1"]
["COP","","","","2.86 (2), 3.48 (1)","2.89 (2), 3.68 (1)","2.89 (2), 3.54 (1)","2.94 (2), 3.77 (1)"]
["Cooling capacity","Nom.","","kW","20.7 (3)","30.9 (3)","41.5 (3)","62.3 (3)"]
["","Max.","","kW","24.7 (3)","36.9 (3)","49.5 (3)","74.3 (3)"]
["EER","","","","2.73 (3)","2.29 (3)","2.69 (3)","2.27 (3)"]
["Heating capacity","Nom.","","kW","21.3 (1), 21.3 (2)","32.1 (1), 32.1 (2)","42.5 (1), 42.5 (2)","63.7 (1), 63.7 (2)"]
["","Max.","","kW","25.3 (1), 25.3 (2)","38.1 (1), 38.1 (2)","50.5 (1), 50.5 (2)","75.7 (1), 75.7 (2)"]
["Power input","Heating","Nom.","kW","6.12 (1), 7.44 (2)","8.72 (1), 11.1 (2)","12.0 (1), 14.7 (2)","16.9 (1), 21.7 (2)"]
["","Cooling","Nom.","kW","7.59 (3)","13.5 (3)","15.4 (3)","27.4 (3)"]
["Notes","","","","(1) - Heating Ta DB/WB 7/6°C - LWC35°C (DT = 5°C), data according EN 14511: 2011","(1) - Heating Ta DB/WB 7/6°C - LWC35°C (DT = 5°C), data according EN 14511: 2011","(1) - Heating Ta DB/WB 7/6°C - LWC35°C (DT = 5°C), data according EN 14511: 2011","(1) - Heating Ta DB/WB 7/6°C - LWC35°C (DT = 5°C), data according EN 14511: 2011"]
["","","","","(2) - Heating Ta DB/WB 7/6°C - LWC45°C","(2) - Heating Ta DB/WB 7/6°C - LWC45°C","(2) - Heating Ta DB/WB 7/6°C - LWC45°C","(2) - Heating Ta DB/WB 7/6°C - LWC45°C"]
["","","","","(3) - Cooling: Ta 35°C - LWE 7°C (DT=5°C), data according EN 14511: 2011","(3) - Cooling: Ta 35°C - LWE 7°C (DT=5°C), data according EN 14511: 2011","(3) - Cooling: Ta 35°C - LWE 7°C (DT=5°C), data according EN 14511: 2011","(3) - Cooling: Ta 35°C - LWE 7°C (DT=5°C), data according EN 14511: 2011"]
["","","","","(4) - Its functioning relies on fluorinated greenhouse gases","(4) - Its functioning relies on fluorinated greenhouse gases","(4) - Its functioning relies on fluorinated greenhouse gases","(4) - Its functioning relies on fluorinated greenhouse gases"]